## 2023 EPA REGION 8 WY SANITARY SURVEY FORM

# INVENTORY

| DATE OF SURVEY: | COUNTY: | SURVEYOR NAME: |
| --- | --- | --- |
| PWS ID: | SYSTEM NAME: |  |
| System representatives (including titles) present at survey: Others present: Comments: |  | EMERGENCY CONTACT Emergency Contact Name: Emergency phone number: ( ) Emergency email address: Title: Business Mailing Address: Street: City: State: Zip: Comments: |
| SYSTEM OWNER OR MUNICIPAL LEGAL REPRESENTATIVE Addressee Name: Title: Company (if Corporation, name of Corporation): Business Mailing Address: Street: City: State: Zip: Business Phone: ( ) Cell Phone: ( ) Email Address: Comments: |  |  |
|  |  | PRIMARY ADMINISTRATIVE CONTACT (to receive ALL correspondence from EPA) Addressee: Title: Business Mailing Address: Street: City: State: Zip: Business Phone: ( ) Cell: ( ) Email Address: Comments: |
| ADDITIONAL CONTACT (if any) Addressee: Title: Business Mailing Address: Street: City: State: Zip: Business Phone: ( ) Cell: ( ) Email Address: Comments: |  | ADDITIONAL CONTACT (if any) Addressee: Title: Business Mailing Address: Street: City: State: Zip: Business Phone: ( ) Cell: ( ) Email Address: Comments: |
| DESIGNATED RESPONSIBLE CHARGE (RC) OPERATOR Name: Operator Certified? Yes No Not required for NC Systems Cert. Level: Area: Exp. Year: Cert. Level: Area: Exp. Year: NA Business Phone: ( ) Cell Phone: ( ) Business Mailing Address: Contract Operator? Yes No Date contract ends: Email Address: Comments: Go to: WYDEQ Operator Certification Website 'Check Operator Records' |  | DESIGNATED SUB. RESPONSIBLE CHARGE (SRC) OPERATOR Name: Operator Certified? Yes No Not required for NC Systems Cert. Level: Area: Exp. Year: Cert. Level: Area: Exp. Year: NA Business Phone: ( ) Cell Phone: ( ) Business Mailing Address: Contract Operator? Yes No Date contract ends: Email Address: Comments: Go to: WYDEQ Operator Certification Website 'Check Operator Records' |
| WATER SYSTEM CLASSIFICATION for WYDEQ Operator Certification WYDEQ System Classification: Not required for NC Systems Level: Area: Level: Area: NA Comments: Go to: WYDEQ Operator Certification Website 'Check Facility Records' |  | WATER SYSTEM CLASSIFICATION from PWS Inventory C = Community NTNC = Non-Transient Non-Community NC = Transient Non-Community Comments: |
| SYSTEM PHYSICAL ADDRESS Street: City: State: Zip: |  | PHYSICAL LOCATION Physical Location and Directions: |
| DEQ DISTRICT ENGINEER , District Engineer Phone: (307) Email: |  | County and/or CHS Sanitarian , CHS Specialist Phone: (307) Email: |
| PERIOD OF OPERATION Year-round Seasonal Operation Dates: From to From to Comments: |  | SERVICE CONNECTIONS Total Service Connections (Active and Inactive): Number of Metered Service Connections? Number of un-metered service connections: Comments: |
| OWNER TYPE 1 Federal Government: National Park, National Forest, etc. 2 Private: Subdivision, Investor, Trust, Cooperative, Water Association, etc. Is this PWS operating with a lease on Federal land? Yes No If Yes, enter name of the Federal land here: 3 State Government 4 Local Government Authority: Commission, District, Municipality, City, etc. 5 Mixed Public/Private 6 Native American: Indian Tribes & Reservations 7 Other Comments: |  | POPULATION DIRECTLY SERVED Average Daily Users (do not include populations of consecutive PWSs) Residential Population (year-round residents): Non-Residential Non-Transient Population: (Over 6 months/year, e.g. employees, students during the peak 60 days of operation) Transient Population (Less than 6 months/year): (Average daily number during peak 60 days of operation, e.g. customers, visitors) Source of population info: Comments: |
| SERVICE CATEGORY (check all that apply) AP Airport PC Picnic Area BA Bathing/Swimming RA Rest Area BR Bar RC Recreation CG Campground RS Residential CH Church RT Restaurant DC Daycare Center RV RV Park DR Dude Ranch SC School HS Hospital SD Subdivision IB Interstate Bottler SK Ski Area IF Industrial/Agricultural SS Service Station IN Institution US Water User's Association LB Local Bottler VC Visitor Center LO Lodge VM Vending Machine MA Marina WH Water Hauler MH Mobile Home Park XX Other MO Motel/Hotel Primary Service Category Description: Comments: |  | SOURCES (check all that apply) SW = Surface Water SWP = Surface Water Purchased GW = Groundwater GWP = Groundwater Purchased GWUDI/GU = GW Under the Direct Influence of SW GWUDIP/GUP = GW Under the Direct Influence of SW Purchased If mixed, does GW receive full SW Treatment? Yes No NA |
|  |  | Is the current water source adequate in quantity? Yes No Describe: Have there been any interruptions in service since the last survey? Yes No Describe: Have there been reports of a water borne disease (2 or more people)? Yes No Describe: Have there been any changes to the water system since the last survey? Yes No Date of Changes: Describe: Are there any changes that are planned? Yes No Projected Date: Describe: Comments: |
| SUMMARY (Describe the water system, including a summary of the water flow through system components from source to distribution) |  |  |
| The following abbreviations will be used throughout this document: NI = no information available, NA = not applicable, NR = not requested, NM = not measured, @ = potential significant deficiency. |  |  |

# SIGNIFICANT DEFICIENCIES

# SIGNIFICANT DEFICIENCIES

Significant deficiencies include, but are not limited to, defects in the design, operation, or maintenance, or a failure or malfunction of the sources, treatment, storage, or distribution system, that the EPA determines to be causing, or have the potential for causing, the introduction of contamination into the water delivered to consumers. Please note the instructions for responding to significant deficiencies in the attached cover letter. Failure to provide a response to the EPA could result in a violation. Prior to making physical modifications to your water system, a permit issued by the Wyoming Department of Environmental Quality (WY DEQ) may be required. Contact the respective WY DEQ District Engineer for your area to determine if a permit is needed before making corrections for significant deficiencies followed by an asterisk (*). The email and phone number for the DEQ District Engineer may be found on Page 2 of your Sanitary Survey Report.

UNCORRECTED SIGNIFICANT DEFICIENCIES FROM PRIOR SANITARY SURVEY

Numbered significant deficiencies and associated numbered photos, if applicable

# RECOMMENDATIONS

Numbered recommendations and associated numbered photos, if applicable

CONSECUTIVE SYSTEMS

(i.e. does this PWS receive some or all of its water from another PWS?)

NA

| Wholesale System | Who is responsible for maintenance of the connection(s)? | Connection Type |
| --- | --- | --- |
| Name: PWSID: Population: Facility ID: How many master meter connections exist from the wholesale system to the consecutive system? | Wholesaler Consecutive system If the consecutive system is responsible, check the condition of the principal master meter and the pit for leaks or flooding and describe any concerns: How often is inspection performed? How often is maintenance performed? Is there standing water in the meter pit/vault? Yes No NA If so, what is the source of the standing water? Leaks @ Groundwater Unknown @ If groundwater, what evidence exists for groundwater as the source? | Permanent Seasonal, # Days/Yr: Emergency Only |
|  | Water Source Type GW SW GU Mixed If mixed, does GW receive full SW Treatment? Yes No NA Type of residual disinfectant in water supplied: Chlorine Chloramines None Type of corrosion inhibitor applied: Orthophosphate Polyphosphate Blend Silicate-based Other: None |  |
| Comments: |  |  |
| Wholesale System | Who is responsible for maintenance of the connection(s)? | Connection Type |
| Name: PWSID: Population: Facility ID: How many master meter connections exist from the wholesale system to the consecutive system? | Wholesaler Consecutive system If the consecutive system is responsible, check the condition of the principal master meter and the pit for leaks or flooding and describe any concerns: how often is inspection performed? how often is maintenance performed? Is there standing water in the meter pit/vault? Yes No NA If so, what is the source of the standing water? Leaks @ Groundwater Unknown @ If groundwater, what evidence exists for groundwater as the source? | Permanent Seasonal, # Days/Yr: Emergency Only |
|  | Water Source Type GW SW GU Mixed If mixed, does GW receive full SW Treatment? Yes No NA Type of residual disinfectant in water supplied: Chlorine Chloramines None Type of corrosion inhibitor applied: Orthophosphate Polyphosphate Blend Silicate-based Other: None |  |
| Comments: |  |  |
| Wholesale System | Who is responsible for maintenance of the connection(s)? | Connection Type |
| Name: PWSID: Population: Facility ID: How many master meter connections exist from the wholesale system to the consecutive system? | Wholesaler Consecutive system If the consecutive system is responsible check the condition of the principal master meter and the pit for leaks or flooding and describe any concerns: how often is inspection performed? how often is maintenance performed? Is there standing water in the meter pit/vault? Yes No NA If so, what is the source of the standing water? Leaks @ Groundwater Unknown @ If groundwater, what evidence exists for groundwater as the source? | Permanent Seasonal, # Days/Yr: Emergency Only |
|  | Water Source Type GW SW GU Mixed If mixed, does GW receive full SW Treatment? Yes No NA Type of residual disinfectant in water supplied: Chlorine Chloramines None Type of corrosion inhibitor applied: Orthophosphate Polyphosphate Blend Silicate-based Other: None |  |
| Comments: |  |  |

If PWS Purchases Water from a WATER HAULER: Name of hauler: WY Dept. of Agriculture license number: Name of the water system supplying water to the hauler: Is there a water tight cap on the (water system’s) fill port? @ Yes No How does the operator check chlorine residual at the time of delivery? Comments:

# WHOLESALE SYSTEMS

(i.e. does this PWS supply water to another PWS?)

NA

| Consecutive System | Who is responsible for maintenance of the connection(s)? | Connection Type |
| --- | --- | --- |
| Name: PWSID: # of master meter connections: Population: Contact and address if no PWSID: | Wholesaler Consecutive system Inspect one representative connection if wholesaler is responsible. If the wholesaler is responsible: how often is inspection performed? how often is maintenance performed? Is there standing water in any meter pit/vault? Yes No NA If so, what is the source of the standing water? Leaks @ Groundwater Unknown @ If groundwater, what evidence exists for groundwater as the source? Comments: | Permanent Seasonal, # Days/Yr Emergency Only Water is hauled (bulk water fill stations are described in Distribution section) |
| Name: PWSID: # of master meter connections: Population: Contact and address if no PWSID: | Wholesaler Consecutive system Inspect one representative connection if wholesaler is responsible. If the wholesaler is responsible: how often is inspection performed? how often is maintenance performed? Is there standing water in any meter pit/vault? Yes No NA If so, what is the source of the standing water? Leaks @ Groundwater Unknown @ If groundwater, what evidence exists for groundwater as the source? Comments: | Permanent Seasonal, # Days/Yr Emergency Only Water is hauled (bulk water fill stations are described in Distribution section) |
| Name: PWSID: # of master meter connections: Population: Contact and address if no PWSID: | Wholesaler Consecutive system Inspect one representative connection if wholesaler is responsible. If the wholesaler is responsible: how often is inspection performed? how often is maintenance performed? Is there standing water in any meter pit/vault? Yes No NA If so, what is the source of the standing water? Leaks @ Groundwater Unknown @ If groundwater, what evidence exists for groundwater as the source? Comments: | Permanent Seasonal, # Days/Yr Emergency Only Water is hauled (bulk water fill stations are described in Distribution section) |
| Comments: |  |  |
| How many master meter connections exist off the wholesale system? |  |  |

# SOURCE DATA

## ACTIVE (PHYSICALLY CONNECTED) WELLS AND WELL PUMPS

(if well is GWUDI and fully treated as SW, these will be recommendations)

NA

| Well Name (according to the system): |  |  |  |
| --- | --- | --- | --- |
| Facility ID (from PWS inventory, e.g., WL01): |  |  |  |
| Well owner (if different than system owner): |  |  |  |
| Well Location: (well house, well pit, pitless adapter, driveway/parking lot, combination, etc.) |  |  |  |
| Does system want this well to be considered inactive? @ | Yes No | Yes No | Yes No |
| Is the well adequately protected from vehicle damage? @ | Yes No | Yes No | Yes No |
| If well is located in a pit or vault, is the pit or vault completely watertight? | Yes No NA | Yes No NA | Yes No NA |
| If no, is the pit or vault completed with drainage or a sump pump for permanent or portable use? @ If applicable, indicate type (permanent pump, portable pump, or drainage) | Yes No NA Type: | Yes No NA Type: | Yes No NA Type: |
| Is the pit located in a building? | Yes No NA | Yes No NA | Yes No NA |
| WY DEQ and/or WY SEO permit #: |  |  |  |
| Are there any approved WY DEQ Chapter 12 variances for this well? If yes, describe what variance was approved. | Yes No | Yes No | Yes No |
| Total Well Depth (ft): |  |  |  |
| Depth range of shallowest casing perforations (ft): | to | to | to |
| Current yield and source of information (gpm): |  |  |  |
| Well log or Statement of Completion on site? (Submit with report and note well SC name here) | Yes No | Yes No | Yes No |
| Well Construction |  |  |  |
| Does SW runoff drain away from the wellhead (including wells in pits or vaults)? @ | Yes No NA | Yes No NA | Yes No NA |
| Does well casing terminate at least 12” above the concrete floor (indoor well)? @ | Yes No NA | Yes No NA | Yes No NA |
| Does the well casing terminate at least 18” above the natural ground surface (outdoor well)? @ | Yes No NA | Yes No NA | Yes No NA |
| What is the actual casing height (inches)? |  |  |  |
| Any holes or openings observed in the well or its appurtenances? @ | Yes No NA | Yes No NA | Yes No NA |
| If yes, describe. |  |  |  |
| Does the well have a sanitary seal with tightly bolted cap? @ (May need operator to open well cap to verify; explain why if unable to verify) | Yes No Unknown | Yes No Unknown | Yes No Unknown |
| Is a gasket visible? | Yes No NA | Yes No NA | Yes No NA |
| Does the well cap move? | Yes No NA | Yes No NA | Yes No NA |
| Explain |  |  |  |
| Is well vented (vent not required)? | Yes No NA | Yes No NA | Yes No NA |
| What is the height from the ground level to the screen of the vent (inches)? |  |  |  |
| Does the vent terminate at or above the top of the casing or pitless unit? @ | Yes No NA | Yes No NA | Yes No NA |
| Is the vent facing downward? @ | Yes No NA | Yes No NA | Yes No NA |
| Is the vent screened with #24-mesh? @ | Yes No NA | Yes No NA | Yes No NA |
| Is there a source water sample tap for GWR compliance? @ | Yes No NA | Yes No NA | Yes No NA |
| Is the tap located prior to any treatment or storage? @ | Yes No NA | Yes No NA | Yes No NA |
| Where is the source water tap located relative to the water system facilities (e.g. pressure tanks; provide photos)? |  |  |  |
| If it is a combined tap: What wells does the sample tap represent? | NA | NA | NA |
| Is there an air release/vacuum relief valve (not required)? | Yes No NA | Yes No NA | Yes No NA |
| Discharge Piping Termination |  |  |  |
| - In a downward position? @ | Yes No NA | Yes No NA | Yes No NA |
| - At least 8” above the floor? @ | Yes No NA | Yes No NA | Yes No NA |
| - Screened with #24-mesh? @ | Yes No NA | Yes No NA | Yes No NA |
| Comments: |  |  |  |
| Well Pumps (Skip if artesian and no pumps) | NA | NA | NA |
| Submersible Pump (if not, describe and indicate location in the comment field below)? | Yes No | Yes No | Yes No |
| Pump Make/Model/HP: |  |  |  |
| Variable frequency drive controlled? If Yes, make/model: | Yes No | Yes No | Yes No |
| Normal operating pressure at pump house (psi): |  |  |  |
| Date pump last replaced: |  |  |  |
| Pump run time at time of visit (min): |  |  |  |
| NSF-60 lubricant used? | Yes No NA | Yes No NA | Yes No NA |
| Maintenance program in place? | Yes No | Yes No | Yes No |
| Is the external pump subject to flooding? @ | Yes No NA | Yes No NA | Yes No NA |
| Spare parts/pump available (specify in comments)? | Yes No NA | Yes No NA | Yes No NA |
| Emergency power available? | Yes No NA | Yes No NA | Yes No NA |
| Comments (include pump operation sounds, leakage observed, pump not operable, operator concerns) |  |  |  |
| Are there any known sources of pollution near the wells which could possibly impact water quality? @ Yes No Examples: Septic systems, chemical storage/mixing facilities, agriculture activities, industrial activities, animal enclosures, cleaning supplies, oil/fuel, etc) If yes, indicate impacted well(s) and provide general location and comments (please locate on aerial map and provide photos): How far from the well is the source of pollution located? Mice or other animals and their droppings in immediate area (well house, vault, pit, etc.)? @ Yes No Are there seasonal variations in the quantity of the water? Yes No Are there seasonal variations in the quality of the water? Yes No How does the system handle sewage? Centralized Sewage Treatment Septic Systems with Pumped Vaults Septic Systems with Leach Fields (mark location on aerial if near well) Comments: |  |  |  |

SOURCE DATA

## ACTIVE (PHYSICALLY CONNECTED) WELLS AND WELL PUMPS

(if well is GWUDI and fully treated as SW, these will be recommendations)

NA

| Well Name (according to the system): |  |  |  |
| --- | --- | --- | --- |
| Facility ID (from PWS inventory, e.g., WL01): |  |  |  |
| Well owner (if different than system owner): |  |  |  |
| Well Location: (well house, well pit, pitless adapter, combination, driveway/ parking lot, other) |  |  |  |
| Does system want this well to be considered inactive? @ | Yes No | Yes No | Yes No |
| Is the well adequately protected from vehicle damage? @ | Yes No | Yes No | Yes No |
| If well is located in a pit or vault, is the pit or vault completely watertight? | Yes No NA | Yes No NA | Yes No NA |
| If no, is the pit or vault completed with drainage or a sump pump for permanent or portable use? @ If applicable, indicate type (permanent pump, portable pump, or drainage) | Yes No NA Type: | Yes No NA Type: | Yes No NA Type: |
| Is the pit located in a building? | Yes No NA | Yes No NA | Yes No NA |
| WY DEQ and/or WY SEO permit #: |  |  |  |
| Are there any approved WY DEQ Chapter 12 variances for this well? If yes, describe what variance was approved. | Yes No | Yes No | Yes No |
| Total Well Depth (ft): |  |  |  |
| Depth range of shallowest casing perforations (ft): | to | to | to |
| Current yield (gpm): |  |  |  |
| Well log or Statement of Completion on site? (Submit with report and note well SC name here) | Yes No | Yes No | Yes No |
| Well Construction |  |  |  |
| Does SW runoff drain away from the wellhead (including wells in pits or vaults)? @ | Yes No NA | Yes No NA | Yes No NA |
| Does well casing terminate at least 12” above the concrete floor (indoor well)? @ | Yes No NA | Yes No NA | Yes No NA |
| Does the well casing terminate at least 18” above the natural ground surface (outdoor well)? @ | Yes No NA | Yes No NA | Yes No NA |
| What is the actual casing height (inches)? |  |  |  |
| Any holes or openings observed in the well or its appurtenances? | Yes No NA | Yes No NA | Yes No NA |
| If yes, describe. |  |  |  |
| Does the well have a sanitary seal with tightly bolted cap? @ (May need operator to open well cap to verify; explain why if unable to verify) | Yes No Unknown | Yes No Unknown | Yes No Unknown |
| Is a gasket visible? | Yes No NA | Yes No NA | Yes No NA |
| Does the well cap move? | Yes No NA | Yes No NA | Yes No NA |
| Explain |  |  |  |
| Is well vented (vent not required)? | Yes No NA | Yes No NA | Yes No NA |
| What is the height from the ground level to the screen of the vent (inches)? |  |  |  |
| Does the vent terminate at or above the top of the casing or pitless unit? @ | Yes No NA | Yes No NA | Yes No NA |
| Is the vent facing downward? @ | Yes No NA | Yes No NA | Yes No NA |
| Is the vent screened with #24-mesh? @ | Yes No NA | Yes No NA | Yes No NA |
| Is there a source water sample tap for GWR compliance? @ | Yes No NA | Yes No NA | Yes No NA |
| Is the tap located prior to any treatment or storage? @ | Yes No NA | Yes No NA | Yes No NA |
| Where is the source water tap located relative to the water system facilities (e.g. pressure tanks; provide photos)? |  |  |  |
| If it is a combined tap: What wells does the sample tap represent? | NA | NA | NA |
| Is there an air release/vacuum relief valve (not required)? | Yes No NA | Yes No NA | Yes No NA |
| Discharge Piping Termination |  |  |  |
| - In a downward position? @ | Yes No NA | Yes No NA | Yes No NA |
| - At least 8” above the floor? @ | Yes No NA | Yes No NA | Yes No NA |
| - Screened with #24-mesh? @ | Yes No NA | Yes No NA | Yes No NA |
| Comments: |  |  |  |
| Well Pumps (Check NA & skip if artesian and no pumps) | NA | NA | NA |
| Submersible Pump (if not, describe and indicate location in the comment field below)? | Yes No | Yes No | Yes No |
| Pump Make/Model/HP: |  |  |  |
| Variable frequency drive controlled? If Yes, make/model: | Yes No | Yes No | Yes No |
| Normal operating pressure at pump house (psi): |  |  |  |
| Date pump last replaced: |  |  |  |
| Pump run time at time of visit (min): |  |  |  |
| NSF-60 lubricant used? | Yes No NA | Yes No NA | Yes No NA |
| Maintenance program in place? | Yes No | Yes No | Yes No |
| Is the external pump subject to flooding? @ | Yes No NA | Yes No NA | Yes No NA |
| Spare parts/pump available (specify in comments)? | Yes No NA | Yes No NA | Yes No NA |
| Emergency power available? | Yes No NA | Yes No NA | Yes No NA |
| Comments (include pump operation sounds, leakage observed, pump not operable, operator concerns) |  |  |  |
| Are there any known sources of pollution near the wells which could possibly impact water quality? @ Yes No Examples: Septic systems, chemical storage/mixing facilities, agriculture activities, industrial activities, animal enclosures, cleaning supplies, oil/fuel, etc) If yes, indicate impacted well(s) and provide general location and comments (please locate on aerial map and provide photos): How far from the well is the source of pollution located? Mice or other animals and their droppings in immediate area (well house, vault, pit, etc.) @ Yes No Are there seasonal variations in the quantity of the water? Yes No Are there seasonal variations in the quality of the water? Yes No How does the system handle sewage? Centralized Sewage Treatment Septic Systems with Pumped Vaults Septic Systems with Leach Fields (mark location on aerial if near well) Comments: |  |  |  |

SOURCE DATA

## SPRINGS AND ASSOCIATED PUMPS

NA

| Spring name: Facility ID (from PWS Inventory, e.g., SPR01): Spring owner if different than system owner: WY DEQ permit number: WY SEO permit number: Are there any approved WY DEQ Chapter 12 variances for this spring? If yes, describe what variance was approved: | Description of the intake to the spring collection box (i.e., how the spring water is collected and conveyed into the box): How often are the spring collection box and spring collection area inspected? Current yield (gpm): Please copy or photograph any available construction diagrams or “as-builts” and submit with the sanitary survey report. Comments: |
| --- | --- |
| SPRING COLLECTION BOX Yes No NA Are the spring collection area and spring box fenced to keep large animals away? @ Does surface water runoff drain away from the collection area? Is there abundant vegetation around the spring collection area and spring box? Describe: Does the spring collection box have the following features: Proper shoe box cover? @ Rubber gasket on the access hatch cover? @ Air vents screened with #24-mesh? @ Is the hatch cover locked? @ Overflow screened with #24-mesh screen? @ Does overflow have a free fall of at least 12 inches? @ Is the spring collection box water tight to prevent inflow of unwanted surface water? @ Comments: | SPRING COLLECTION INFORMATION Depth to water: ft NI Depth to intake pipe: ft NI Do water levels in the collection device change? Yes No NI Are the changes seasonal? Yes No NI Does water rise to the surface within 100 ft of the source during parts of the year? Yes No NI Comments: SOURCE PUMPS Location of the pump station: How many pumps at the facility? Type of pump(s): Yes No NA Are the correct types of lubricants (NSF-60) used? Are pumps operable and in good condition? Is there a maintenance program in operation? Is the pump station subject to flooding? @ Are spare parts available? Is emergency power available? Comments: |
| For any other hatches/manholes that are part of the spring collection system or on the transmission line from the spring box to a storage tank or distribution system: (describe the condition of each) NA Proper shoe box cover on the access hatch/manhole? @ Yes No Description and location: Rubber gasket on the access hatch/manhole cover? @ Yes No Is the hatch cover locked? @ Yes No |  |
| Is there a source water sample tap for GWR compliance? @ Yes No NA |  |
| Is the tap located prior to any treatment or storage? @ Yes No NA |  |
| Where is the source water tap located relative to the water system facilities (e.g. pressure tanks; provide photos)? |  |
| If it is a combined tap: NA What sources does the sample tap represent? |  |
| Are there any known sources of pollution near the springs which could possibly impact water quality? @ Yes No (Examples: Septic systems, chemical storage/mixing facilities, agriculture activities, industrial activities, animal enclosures, cleaning supplies, oil/fuel, etc) If yes, indicate impacted spring(s) and provide general location and comments (please locate on aerial map and provide photos): How far from the spring is the source of pollution located? Mice or other animals and their droppings in immediate area (spring house, etc.)? @ Yes No Are there seasonal variations in the quantity of the water? Yes No Are there seasonal variations in the quality of the water? Yes No How does the system handle sewage? Centralized Sewage Treatment Septic Systems with Pumped Vaults Septic Systems with Leach Fields (mark location on aerial if near spring) Comments: |  |

SOURCE DATA FOR INTAKE LOCATED IN

## INFILTRATION GALLERIES AND ASSOCIATED PUMPS

NA

| INFILTRATION GALLERIES Infiltration gallery name: Facility ID (from PWS Inventory, e.g., IG01): Infiltration gallery owner if different than system owner: WY DEQ permit number: WY SEO permit number: Physical description: How often are infiltration gallery components inspected? Depth? Current yield (gpm): Are there seasonal algal blooms present? Yes No Describe: Is an algaecide ever used to control algae? Yes No If yes, describe: Please copy or photograph any available construction diagrams or “as-builts” and submit with the sanitary survey report | INFILTRATION GALLERY COLLECTION INFORMATION Depth to water: ft NI Depth to intake pipe: ft NI Do water levels in the collection device change? Yes No NI Are the changes seasonal? Yes No NI Does water rise to the surface within 100 ft of the source during parts of the year? Yes No NI Comments: SOURCE PUMPS Location of the pump station: How many pumps at the facility? Type of pump(s): Yes No NA Are the correct types of lubricants (NSF-60) used? Are pumps operable and in good condition? Is there a maintenance program in operation? Is the pump station subject to flooding? Are spare parts available? Is emergency power available? Comments: |
| --- | --- |
| Are there any known sources of pollution near the infiltration gallery (e.g., agriculture/industrial activities, cleaning supplies, oil/fuel, etc.) which could impact water quality? @ Yes No If yes, indicate impacted infiltration gallery/galleries and provide general location and comments (please locate on aerial map and provide photos): How far from the infiltration gallery is the source of pollution located? Are there seasonal variations in the quantity of the water? Yes No Are there seasonal variations in the quality of the water? Yes No Comments: |  |

SOURCE DATA FOR INTAKE LOCATED IN

## STREAMS, AND ASSOCIATED PUMPS

NA

| STREAMS Stream name: Facility ID (from PWS Inventory, e.g., IN01): WY DEQ permit number: WY SEO permit number: Is the area around the intake restricted? Yes No Are there multiple intakes located at different levels? Yes No Describe: Are the intake(s) screened? Yes No Frequency of intake inspection: Date of last inspection: Are there seasonal algal blooms present? Yes No Describe: Is an algaecide ever used to control algae? Yes No If yes, describe: Please copy or photograph any available construction diagrams or “as-builts” and submit with the sanitary survey report | INTAKE PUMPS Location of the pump station: How many pumps at the facility? Type of pump(s): Yes No NA Are the correct types of lubricants (NSF-60) used? Are pumps operable and in good condition? Is there a maintenance program in operation? Is the pump station subject to flooding? Are spare parts available? Is emergency power available? Comments: |
| --- | --- |
| Are there any known sources of pollution near the stream (e.g., agriculture/industrial activities, cleaning supplies, oil/fuel, etc.) which could impact water quality? @ Yes No If yes, indicate impacted stream(s) and provide general location and comments (please locate on aerial map and provide photos): How far from the stream is the source of pollution located? Are there seasonal variations in the quantity of the water? Yes No Are there seasonal variations in the quality of the water? Yes No Comments: |  |

SOURCE DATA FOR INTAKE LOCATED IN

## RESERVOIRS, LAKES AND PONDS AND ASSOCIATED PUMPS

NA

| Reservoir or lake name: Facility ID (from PWS Inventory, e.g., IN01): WY DEQ permit number: WY SEO permit number: |  |
| --- | --- |
| RESERVOIRS Is the area around the intake(s) restricted? Yes No Are there multiple intakes located at different levels? Yes No Describe: Depth of intake(s): Distance from shore: Are the intake(s) screened? Yes No Frequency of intake inspection: Date of last inspection: Are there seasonal algal blooms present? Yes No Describe: Is an algaecide ever used to control algae? Yes No If yes, describe: Please copy or photograph any available construction diagrams or “as-builts” and submit with the sanitary survey report | INTAKE PUMPS Location of the pump station: How many pumps at the facility? Type of pump(s): Yes No NA Are the correct types of lubricants (NSF-60) used? Are pumps operable and in good condition? Is there a maintenance program in operation? Is the pump station subject to flooding? Are spare parts available? Is emergency power available? Comments: |
| Are there any known sources of pollution near the reservoir/lake/pond (e.g., agriculture/industrial activities, cleaning supplies, oil/fuel, etc.) which could impact water quality? @ Yes No If yes, indicate impacted reservoir/lake/pond(s) and provide general location and comments (please locate on aerial map and provide photos): How far from the reservoir/lake/pond is the source of pollution located? Are there seasonal variations in the quantity of the water? Yes No Are there seasonal variations in the quality of the water? Yes No Comments: |  |

SOURCE DATA

## EMERGENCY BACKUP SOURCE WATER

Describe any backup source water possibly available during an emergency to the PWS, or indicate none: Is the backup water source physically disconnected from the water system? Yes No (if this is a raw water source and is still physically connected to the system, then stop filling out this section and complete the applicable source data section)

Backup source name: Facility ID (from PWS Inventory, e.g., IN01, WL01, etc.): WY DEQ permit number: WY SEO permit number: Are there seasonal algal blooms present? Yes No NA Describe: Is an algaecide ever used to control algae? Yes No NA If yes, describe: Please copy or photograph any available construction diagrams or “as-builts” and submit with the sanitary survey report

Are there any known sources of pollution near the emergency backup source (e.g., agriculture/industrial activities, cleaning supplies, oil/fuel, etc.) which could impact water quality? @ Yes No If yes, indicate impacted emergency backup source(s) and provide general location and comments (please locate on aerial map and provide photos): How far from the emergency backup source is the source of pollution located? Mice or other animals and their droppings in immediate area (well house, vault, pit, etc.)? Yes No Are there seasonal variations in the quantity of the water? Yes No Are there seasonal variations in the quality of the water? Yes No Comments:

# RAW WATER TO TREATMENT PLANT TRANSMISSION LINE

NA

Name or designation: SW GW GU Point of origin: Point of termination: Approximate Length: Material:

Is there asbestos pipe in the water system between the source and the treatment plant? Yes No If yes, what are the location and estimated linear feet of the asbestos pipe in the transmission line? Has all of the asbestos pipe been removed? Yes No NA If so, when was it removed?

Are there any service connections off the raw water transmission line? @ Yes No (Check yes only if the water system provides treated water to the rest of the distribution system) What does each connection serve? NA If used for potable water supply, is there a legal agreement or contract in place? Yes No NA If used for potable water supply, is the water treated at the connection and how? Yes No NA

Name or designation: SW GW GU Point of origin: Point of termination: Approximate Length? Material:

Is there asbestos pipe in the water system between the source and the treatment plant? Yes No If yes, what are the location and estimated linear feet of the asbestos pipe in the transmission line? Has all of the asbestos pipe been removed? Yes No NA If so, when was it removed?

Are there any service connections off the raw water transmission line? @ Yes No (Check yes only if the water system provides treated water to the rest of the distribution system) What does each connection serve? NA If used for potable water supply, is there a legal agreement or contract in place? Yes No NA If used for potable water supply, is the water treated at the connection and how? Yes No NA

# WATER TREATMENT DATA

## GROUNDWATER AND CONSECUTIVE SYSTEMS THAT HAVE AVAILABLE TREATMENT

NA

| Describe the steps (as many as necessary) of the treatment process in order from the water source to distribution: Plant Output (gal/day) Design: Maximum: Any changes to treatment since the last sanitary survey? Yes No Describe: |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Step 1 | Step 2 | Step 3 | Step 4 |
| Process | Chemical Manufacturer Product Name (photograph the product label) Yes No NSF 60 Certified? UV Filtration; type: Ion exchange Softener Other: Dosage: | Chemical Manufacturer Product Name (photograph the product label) Yes No NSF 60 Certified? UV Filtration; type: Ion exchange Softener Other: Dosage: | Chemical Manufacturer Product Name (photograph the product label) Yes No NSF 60 Certified? UV Filtration; type: Ion exchange Softener Other: Dosage: | Chemical Manufacturer Product Name (photograph the product label) Yes No NSF 60 Certified? UV Filtration; type: Ion exchange Softener Other: Dosage: |
| NSF 60 certification and max. allowable dose info. can be found at: http://info.nsf.org/Certified/PwsChemicals/ |  |  |  |  |
| Objective: | Disinfection Particulate removal Hardness removal Taste & odor removal Metals removal Nitrate removal Corrosion control Other: | Disinfection Particulate removal Hardness removal Taste & odor removal Metals removal Nitrate removal Corrosion control Other: | Disinfection Particulate removal Hardness removal Taste & odor removal Metals removal Nitrate removal Corrosion control Other: | Disinfection Particulate removal Hardness removal Taste & odor removal Metals removal Nitrate removal Corrosion control Other: |
| Is this process required by EPA? | Yes No | Yes No | Yes No | Yes No |
| Location of process? | At Well At Treatment Plant Other: | At Well At Treatment Plant Other: | At Well At Treatment Plant Other: | At Well At Treatment Plant Other: |
| Is this process adequate to meet the objective? | Yes No Explain: | Yes No Explain: | Yes No Explain: | Yes No Explain: |
| Frequency of use: | Permanent Seasonal Emergency Other: | Permanent Seasonal Emergency Other: | Permanent Seasonal Emergency Other: | Permanent Seasonal Emergency Other: |
| Redundant Equipment? | Yes No Explain: | Yes No Explain: | Yes No Explain: | Yes No Explain: |
| Backup power? | Yes No Explain: | Yes No Explain: | Yes No Explain: | Yes No Explain: |

Groundwater and Consecutive Systems

### UV Disinfection

Yes No Is there a flow meter to monitor/alarm or a flow restrictor valve so the max flow rate is not exceeded? Describe how the system ensures the flow does not exceed max flow rate: Is there an intensity sensor and alarm (visible/audible) to indicate low intensity? Is there a UV lamp status alarm (visible/audible) to indicate lamps off? Is there a UV lamp age counter/alarm? Is there an automatic shut-off fail-safe solenoid valve so that water does not flow through the unit without adequate treatment? Are there spare bulbs on hand? How often are the unit cleaned and the bulbs changed?

Point of Use Treatment

For PWSs with required Point of Use (POU) treatment, ask the operator – Yes No NA Is the system adhering to the O&M Plan approved by EPA and conducting maintenance according to the manufacturer’s recommendations? Please describe the O&M practices in place and the records that are maintained: (i.e. Is the operator replacing POU filters in accordance with the maintenance plan or manufacturer recommendations, etc.). Is the system following its EPA-approved POU sampling plan? If No, explain any difficulties: Comments:

WATER TREATMENT DATA

## SURFACE WATER / GWUDI SYSTEMS

NA

### General Information

| For each treatment plant indicated on the overall PWS schematic, update the separate treatment plant schematic. Show all treatment processes, recycle streams, turbidimeter locations, raw water and finished water sampling points, and disinfectant residual sampling points. In this section, the ¥ symbol indicates a potential violation to be determined by the EPA Rule Manager |  |
| --- | --- |
| Plant Location and Information Plant / Office Location and Directions: Date plant put online: Modifications since the last survey? (if yes, describe) Yes No Describe water sources treated by this plant: Is treatment impacted by algae (describe)? | Plant Output (gal / day) Design: Summer Average: Winter Average: Maximum: |
| Provide a brief description of the plant’s treatment processes: |  |
| Indicate all points in the treatment process where flow is determined and describe how (i.e. flowmeters, flow restrictors, valves, etc): |  |
| Please indicate all of the treatment plant waste disposal methods the plant currently employs: Discharge to surface, sewer, or equivalent. Please describe: On-site disposal. Please describe: Land application Discharge to lagoon/drying bed, with no recovery/recycling – e.g., downstream outfall Backwash recovery/recycling: discharge to basin or lagoon and then to source Backwash recovery/recycling: discharge to basin or lagoon and then to plant intake Other. Please describe: No wastes generated |  |

### Pre-Filtration Processes

Pre-Sed Basin: Yes No Describe Type and indicate volume, list facility ID if one is assigned: Chemicals added: Yes No (If yes, input chemical information in table below) Rapid Mix: Yes No Describe Type: Chemicals added: Yes No (If yes, input chemical information in table below) Flocculation: Yes No Describe Type: Chemicals added: Yes No (If yes, input chemical information in table below) Sedimentation: Yes No Describe Type: Chemicals added: Yes No (If yes, input chemical information in table below) Other: Yes No Describe: Chemicals added: Yes No (If yes, input chemical information in table below) Chemical Information (ask system to provide information from chemical supplier / manufacturer): Manufacturer; Product Name; Location Chemical Added; Max Dose Used (past 12 months):; NSF 60 Certified?; NSF 60 Max Allowable Dose. Yes No. Yes No. Yes No. Yes No. Yes No. NSF 60 certification and max. allowable dose info. can be found at: http://info.nsf.org/Certified/PwsChemicals/ Does the system use a chemical containing epichlorohydrin or polyacrylamide that is dosed in excess of the NSF 60 Max Allowable Dose? ¥ Yes No

### Filtration Processes

#### General

Indicate all types of filtration used: Conventional Bags / Cartridges Slow Sand Direct Membranes Diatomaceous Earth Which is the final filtration barrier?:

Type and model # of combined filter effluent (CFE) turbidimeter: Location of CFE turbidimeter: Frequency of all turbidimeter calibration(s): Date(s) of last turbidimeter calibration(s) for all turbidimeters: Method used for all calibrations (primary formazin standard or other)? Yes No Does the location of the CFE turbidimeter comply with EPA policy SWTR #5? @ Are turbidimeters calibrated at least once every quarter? @ Does the system use a primary standard to perform the calibration? @ Are CFE turbidity records available for the last 5 years? ¥ Can CFE turbidities be recorded up to 5 NTU? @ How high can they be recorded: Can turbidities associated with off-periods (backwash, FTW) be identified so they are not counted for compliance? (if applicable) @ Finished water CFE turbidity (NTU): PWS measurement: Surveyor measurement: Time of analysis:

#### Conventional and Direct Filtration

| Filter Information # of filters: Type of filters: open to atmosphere enclosed (pressure) Manufacturer name & model (if applicable): Depth of each media (in): Sand: Anthracite: Garnet: Total at least 24”? @ Yes No Has operator observed loss of media? Has the operator inspected the media for mudball formation? Average length of filter run (hours): Maximum filter loading rate (gpm/ft2): Is the filtration rate less than 2 gpm/sf (mono-media), 4 gpm/sf (dual media) or 6 gpm/sf (deep bed)? @ Yes No | Backwash Information What determines when backwash occurs? Backwash rate (gpm/ft2): What is used for a backwash? Air scour finished water raw water @ Yes No System starts up with clean filters (if not running 24/7) System performs filter to waste (FTW) before putting filters back online. |
| --- | --- |

##### Conventional and Direct IFE and CFE additional information (only if final barrier)

IFE Questions NA How are IFE records maintained? SCADA strip chart circular chart Yes No NA Does each filter have an individual effluent (IFE) turbidimeter? ¥ Types and model #s: Are there alarms on each filter? Alarm set point (NTU): Are IFE turbidities measured continuously, and recorded at least every 15 Minutes? ¥ Is IFE turbidity recorder (SCADA or charts) calibrated to record turbidities ≥ 2 NTU? @ Are IFE records kept for the last 3 years (as applicable)? ¥ Did any single filter IFE exceed 1.0 NTU in 2 consecutive 15-minute readings during the last 12 months? If yes, Indicate dates of all occurrences and copy those records. a. If so, did they report to EPA and do a filter profile, if required? ¥ b. If this occurred 3 months in a row, did they conduct a filter self-assessment? ¥ Did any single filter IFE exceed 2.0 NTU in 2 consecutive 15-minute readings in the last 12 months? Indicate dates of all occurrences and copy those records. a. If this occurred 2 months in a row for the same filter, did they report to EPA and have a CPE performed? ¥ For systems serving > 10,000, did the IFE of any filter exceed 0.5 NTU in 2 consecutive 15-minute readings after being online 4 hours (following backwash or other reason offline) in the last 12 months? Indicate dates of all occurrences and copy those records. a. If so, did they report to EPA and do a filter profile, if required? ¥ CFE Questions How are CFE records maintained? SCADA strip chart circular chart Yes No Based on these records, has the system consistently met the CFE turbidity requirements for this type of filtration during the last 12 months? ¥ (0.3 NTU 95% of each month, 1 NTU max) If no, indicate date of all occurrences and copy those records:

Log removal credited for this type of filtration barrier for: Giardia: Viruses: Cryptosporidium:

##### Conventional and Direct (only if filter backwash, thickener supernatant, or sludge dewatering liquid is recycled)

Describe where recycle enters treatment process: Yes No Is recycle location before the TOC monitoring point? Are records of recycle practices kept in an acceptable format for each year that includes all of the required elements (e.g., avg and max times/flows of backwashes; recycle treatment/equalization [chemical addition; hydraulic loading rates])? ¥

#### Membranes

Number of membrane skids: Configuration: parallel series Membrane type: microfiltration ultrafiltration nanofiltration RO Manufacturer: Model #: Absolute pore size: Each skid capacity (gpm): Yes No Has the PWS consistently been meeting the CFE turbidity requirements for this type of filtration? (0.3 NTU 95% of each month, 1 NTU max) ¥ Are direct integrity tests (DIT) performed at least daily (specify pressure or vacuum applied)? ¥ If yes, how often? ¥ For continuous indirect integrity testing, does each unit/skid have its own online turbidimeter? ¥ a. Is filtrate turbidity monitored continuously and recorded at least once every15 minutes? ¥ b. Is it set with a trigger level of 0.15 NTU for > 15 minutes (a DIT should be initiated when filtrate turbidity exceeds this level)? ¥ Do operators know how to check and repair membranes when a DIT fails? @ How/when are membranes cleaned? Are spare membrane cassettes available? Yes No Is there adequate storage of cleaning chemicals in case of emergency weather?

Log removal credited for this type of filtration barrier for: Giardia: Viruses: Cryptosporidium:

#### Bags / Cartridges

Number of parallel filter trains: Each train capacity (gpm): Pre Filter (if applicable) Housing: Manufacturer: Model: Bag / Cartridge Filter: Manufacturer: Model: # per housing: Final Filter Housing: Manufacturer: Model: Bag / Cartridge Filter: Manufacturer: Model: # per housing: Manufacturer’s recommended maximum flow rate (gpm): Pore size rating (microns - indicate absolute or nominal): Replacement frequency of all filters: Yes No Has the PWS consistently been meeting the CFE turbidity requirements for this type of filtration? (1 NTU 95% of each month, 5 NTU max) ¥ Are there working pressure gauges before and after filters? @ Does the PWS keep daily records of monitoring the pressure drop across the filters, and know when to change out filters? @ Has the final filter or pre/final filter combination been demonstrated to remove at least 99.9% of Cryptosporidium or equivalent size particles or have a 1 or 2 micron absolute pore size rating? (leave blank if unknown) @ Does the flow rate through the final filter exceed the manufacturer’s maximum recommended flow rate? @

Log removal credited for this type of filtration barrier for: Giardia: Viruses: Cryptosporidium:

#### Diatomaceous Earth Filters

Number of filters: Pressure System Vacuum System Filter manufacturer/model # (if applicable): Each filter capacity (gpm): Describe pre-coat and body feed systems: Has the PWS consistently been meeting the CFE turbidity requirements for this type of filtration? (1 NTU 95% of each month, 5 NTU max) ¥ Yes No Describe precoat and body feed systems: Maximum filter loading rate (gpm/ft2): Is the filtration rate less than 1.5 gpm/sf? @ Yes No Maximum head loss allowed: What determines when backwash occurs? time turbidity automatic head loss

Log removal credited for this type of filtration barrier for: Giardia: Viruses: Cryptosporidium:

#### Slow Sand Filtration

Number of filters: Each Filter capacity (gpm): What is rate of filtration (gpm/ft)? Is the filtration rate less than 0.1 gpm/sf? @ Yes No Yes No Has the PWS consistently been meeting the CFE turbidity requirements for this type of filtration? (1 NTU 95% of each month, 5 NTU max) ¥ Is turbidity of raw water to filters always <10 NTU? @ Is water depth over sand at least 3 feet during operation? @ Can plant meet design capacity with one unit out of service? Do they ripen after scraping (filter to waste) and how long? Is head loss across filters monitored and used for process control? @ If yes, how is the head loss monitored? How often is each unit scraped?

Log removal credited for this type of filtration barrier for: Giardia: Viruses: Cryptosporidium:

### Disinfection Processes

#### General

Describe all inactivation processes, both pre-filtration and post-filtration:

#### UV Disinfection

Point of application: UV manufacturer/model #: Validated maximum flow (gpm): Validated UV dosage (mJ/cm2): Log inactivation credited based upon validated dosage (use table below): Giardia: Cryptosporidium: Table 1. UV Dose Requirements in Millijoules per Square Centimeter (mJ/cm2) Target Pathogen; Log Inactivation. 0.5; 1.0; 1.5; 2.0; 2.5; 3.0; 3.5; 4.0. Cryptosporidium; 1.6; 2.5; 3.9; 5.8; 8.5; 12; 15; 22. Giardia; 1.5; 2.1; 3.0; 5.2; 7.7; 11; 15; 22. Viruses; **; **; **; **; **; **; **; **. Source: 40 CFR 141.720(d) ** UV not credited with virus inactivation by EPA R8 for SW/GU systems Yes No Does PWS keep records of UV reports sent monthly to EPA? ¥ Does public water system’s Emergency Response Plan address breakage of UV lamps? (Mercury hazard: OSHA guidelines 1910 Subparts H, I, Z, Response to breakage, Cleanup and disposal)

##### UV Disinfection – less than or equal to 40 gpm

Yes No Is there a flow meter to monitor/alarm or a flow restrictor valve so the max flow rate is not exceeded? @ Describe how the system ensures the flow does not exceed max flow rate: Is there an intensity sensor and alarm (visible/audible) to indicate low intensity? @ Is there a UV lamp status alarm (visible/audible) to indicate lamps off? @ Is there a UV lamp age counter/alarm? @ Is there an automatic shut-off fail-safe solenoid valve so that water does not flow through the unit without adequate treatment? @ Does this UV unit have an NSF Standard 55A Certification or has it been validated according to the requirements of the 2006 UV Disinfection Guidance Manual? ¥ (leave blank if unknown) Are there spare bulbs on hand? How often is the unit cleaned and the bulbs changed?

##### UV Disinfection – greater than 40 gpm

How is unit monitored? Intensity Setpoint Method Calculated Dose Method Yes No Is the calibration of the UV intensity sensors checked at least monthly using a reference sensor? @ How frequently are calibration checks performed? Is the calibration of the UV transmittance analyzer checked at least weekly with a benchtop analyzer (Calculated Dose Method only)? @ How frequently are calibration checks performed? Is there a calibrated flowmeter to ensure max flow rate is not exceeded? @ Are daily operational records kept of flow rates/production, run time, lamp status, UV intensity, UVT and UV dosage? ¥ (These should be monitored continuously and recorded at least once/4 hours. Small systems (less than 500 population) are allowed to record one time each day.) Does the operator know how to identify an off-specification event and report it to the EPA? @ Does the system alarm when an off-specification event occurs? @ Are there spare bulbs on hand?

#### Chemical Disinfection

##### Chlorine and Chloramines

Type: Dosage: (lb / day or mg/L) NSF 60 Certified? Yes No Point of application: Where does the PWS measure disinfectant residual for compliance with the SWTR requirement of ≥ 0.2 mg/L at the POE? Is this before the 1st user of the water? ¥ Yes No How is residual measured? continuous grab Equipment / manufacturer model #: What type of measurement is taken? free total (systems that use chloramination must measure total) Chlorine residual at POE (mg/L): PWS measurement: Surveyor measurement: Time of analysis: Are the two measurements within 0.1 mg/L or 15% of one another (whichever is larger)? @ Yes No Yes No Is there redundant disinfection equipment? Is there emergency power for the disinfection equipment? If measuring residual continuously, is the PWS conducting weekly verifications with a grab sample measurement? @

##### Ozone

Number of Ozone generators: Percent ozone being generated (%): Where is the ozone applied? Where is residual measured? Ozone residual (%): Ozone residual (mg/L): Describe the purpose of the ozone addition: Are all applicable residual monitors operational? Are excess ozone destructors operational? Is there a preventive maintenance program for the generators? Is a SCBA or supplied-air respirator available for the operators when working with ozone? Are operators exposed to ozone levels above 0.1 mg/L? Does the system monitor bromate concentration at point of entry? ¥ Yes No

##### Chlorine Dioxide

Number of Chlorine Dioxide generators: Where is the Chlorine Dioxide applied? Where is Chlorine Dioxide residual measured? Chlorine Dioxide residual (mg/L): Describe the purpose of the Chlorine Dioxide addition: Are all applicable residual monitors operational? Is there a preventive maintenance program for the generators? Are operators exposed to Chlorine Dioxide levels above 0.1 ppm? Yes No Does the system monitor chlorine dioxide daily at point of entry? ¥ Does the system monitor chlorite at point of entry daily and monthly in the distribution system? ¥

#### Chemical Disinfection – Inactivation Calculations

| If the PWS performs ongoing daily or weekly CT calculations, use their actual data to document inactivation in the section below. Otherwise, do a conservative calculation for each inactivation segment. Identify location of 1st user: |  |
| --- | --- |
| Summer Calculations Lowest* disinfectant residual and where measured (mg/L): Water temperature (lowest*): °C Water pH (highest*): Maximum* flow through segment: gpm Describe each segment and list appropriate baffling factor: | List the volume of each segment using minimum* operating heights of tanks: Total logs Giardia inactivation from all chemical disinfection segments: Total logs virus inactivation from all chemical disinfection segments: |
| Winter Calculations Lowest* disinfectant residual and where measured (mg/L): Water temperature (lowest*): °C Water pH (highest*): Maximum* flow through segment: gpm Describe each segment and list appropriate baffling factor: | List the volume of each segment using minimum* operating height of tanks: Total logs Giardia inactivation from all chemical disinfection segments: Total logs virus inactivation from all chemical disinfection segments: |
| * Use data from system’s ongoing CT calculations if available. Values should correlate to the system’s lowest calculated inactivation levels during the specified season in the previous year. |  |

#### Chemical Disinfection – Disinfection Profiling (if system is exempt, skip section)

Yes No Does the system have a disinfection profile on site that contains a year of weekly log inactivation calculations (<10,000 pop.) or a year of daily log inactivation calculations (>10,000 pop)? @ Did the PWS make a significant change (new disinfectant; new location; etc.) to disinfection practices after 7/1/03 or 1/1/04? If yes, was EPA consulted? Describe the change and date made: ¥ When was the profile conducted? to Lowest monthly average log inactivation observed from the profile (month/value): Giardia: Viruses:

### Overall Inactivation / Removal Calculations

#### Viruses / Giardia

| Viruses Logs Removal (filtration) Logs chemical inactivation (lowest value from Summer / Winter calculations) Logs UV inactivation Logs other removal or inactivation Total logs inactivation / removal > 4 logs? @ Yes No | Giardia Logs Removal (filtration) Logs chemical inactivation (lowest value from Summer / Winter calculations) Logs UV inactivation Logs other removal or inactivation Total logs inactivation / removal > 3 logs? @ Yes No |
| --- | --- |

#### Cryptosporidium

Committed to install maximum treatment? Yes No If no, what is the system’s bin #? Bin #1 Bin #2 Bin #3 Bin #4 System Classification: Filtered Unfiltered *If system completed sampling and was classified as a Bin #1 system, the section below does not need to be completed. For all other systems, please complete the section below.

Total logs Cryptosporidium inactivation / removal required based on max treatment, bin # or classification: Date treatment required by: Toolbox Components Utilized: Logs Removal (filtration) Logs chemical inactivation Logs UV inactivation Logs other Toolbox Components Total logs inactivation / removal > required logs? ¥ Yes No

# WATER TREATMENT DATA (FOR ALL SYSTEMS)

## CORROSION CONTROL

| Does this PWS add chemicals for corrosion control (If yes, photograph the corrosion control system)? Yes No Type of corrosion inhibitor applied: Orthophosphate Polyphosphate Blend Silicate-based Other: Comments: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Chemical added: | NSF 60 Certified? | Dosage at Treatment Plant | Type of System | Added Continuously or Seasonally |
|  | Yes No |  | Flow-based Constant feed | Continuously Seasonally Other (Specify in comments) |
|  | Yes No |  | Flow-based Constant feed | Continuously Seasonally Other (Specify in comments) |
|  | Yes No |  | Flow-based Constant feed | Continuously Seasonally Other (Specify in comments) |
|  | Yes No |  | Flow-based Constant feed | Continuously Seasonally Other (Specify in comments) |
| Does this PWS monitor corrosion control treatment chemical concentrations, pH or any other water quality parameters at the entry point to the distribution system or at customer taps to evaluate the process? Yes No If yes, what parameters are measured, where are samples taken, and how often? Comments: |  |  |  |  |

# STORAGE TANKS

NA

| Complete for all tanks at ground water systems and consecutive systems. Also complete for finished water tanks at surface water / GWUDI systems. (Includes indoor clearwells and contact tanks or other finished water tanks.) |  |  |  |
| --- | --- | --- | --- |
| Tank Name: |  |  |  |
| Tank ID (from PWS inventory, e.g., ST01): |  |  |  |
| Tank owner (if different than system owner): |  |  |  |
| Location (indoor or outdoor): |  |  |  |
| Date put into service: |  |  |  |
| Tank Type Below ground (buried or partially buried) Ground level Elevated (pedestal or standpipe) |  |  |  |
| Tank is constructed of: Concrete Steel Fiberglass Other |  |  |  |
| What type of water is stored (GW systems only)? NA | Treated Raw | Treated Raw | Treated Raw |
| Storage volume (gallons)? |  |  |  |
| Are there any approved WY DEQ Chapter 12 variances for this tank? If yes, describe what variance was approved. | Yes No | Yes No | Yes No |
| Is the site subject to flooding? @ | Yes No | Yes No | Yes No |
| Can the tank be isolated from the system? | Yes No | Yes No | Yes No |
| Is the water level indicator accurate? | Yes No NA | Yes No NA | Yes No NA |
| Does the tank have a mixer? | Yes No | Yes No | Yes No |
| Does the tank appear structurally sound? @ | Yes No | Yes No | Yes No |
| Does the foundation appear structurally sound? @ | Yes No NA | Yes No NA | Yes No NA |
| Are there unprotected openings in the tank (breaches, leaks, etc.)? @ | Yes No | Yes No | Yes No |
| Inspection and cleaning history |  |  |  |
| How often are the tank hatch, vent, and overflow visually inspected? |  |  |  |
| If the tank is more than 10 years old, was it cleaned and inspected within the last 10 years? @ | Yes No NA | Yes No NA | Yes No NA |
| When and how was the tank last cleaned and inspected? |  |  |  |
| Who performed the cleaning and inspection? |  |  |  |
| How was the tank disinfected after cleaning? (NA if diver used) |  |  |  |
| Surveyor able to view report and confirm date? | Yes No | Yes No | Yes No |
| If yes, note major concerns and/or recommendations: |  |  |  |
| If Carcasses or other debris found in the tank: |  |  |  |
| Was EPA notified immediately? | Yes No | Yes No | Yes No |
| Was the entry point for the carcass or debris eliminated? | Yes No | Yes No | Yes No |
| Describe: |  |  |  |
| Overflow |  |  |  |
| Does the tank have an overflow separate from the vent? @ | Yes No NA | Yes No NA | Yes No NA |
| Is the overflow accessible for inspection? @ | Yes No NA | Yes No NA | Yes No NA |
| Overflow has a #24-mesh screen OR a duckbill valve OR a properly sealed flapper valve with screen of any size inside (EPA recommends non-corrodible #24-mesh screen)? @ | Yes No NA | Yes No NA | Yes No NA |
| Does the overflow line terminate no less than 12 inches but no more than 24 inches above the ground surface? @ | Yes No NA | Yes No NA | Yes No NA |
| Does the overflow discharge over an inlet structure, splash plate, or engineered rip-rap? @ | Yes No NA | Yes No NA | Yes No NA |
| Is the discharge visible? | Yes No NA | Yes No NA | Yes No NA |
| Does the overflow have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? @ | Yes No NA | Yes No NA | Yes No NA |
| Comments about overflow: |  |  |  |
| Drain Line |  |  |  |
| Combined overflow and drain pipe? (If yes, skip drain questions) | Yes No NA | Yes No NA | Yes No NA |
| Is the drain accessible for inspection? @ | Yes No NA | Yes No NA | Yes No NA |
| Is there #24-mesh screen on the drain pipe? | Yes No NA | Yes No NA | Yes No NA |
| Does water accumulate in the drain discharge area? | Yes No NA | Yes No NA | Yes No NA |
| Does the drain pipe have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? @ | Yes No NA | Yes No NA | Yes No NA |
| Does the drain pipe terminate between 12 and 24 inches above a drainage area? | Yes No NA | Yes No NA | Yes No NA |
| Does the drain pipe terminate above an inlet structure, splash plate, or engineered rip-rap? | Yes No NA | Yes No NA | Yes No NA |
| Comments about drain: |  |  |  |
| Air Vent |  |  |  |
| Does the tank have a vent separate from the overflow? @ | Yes No NA | Yes No NA | Yes No NA |
| Is the vent accessible for inspection? @ | Yes No NA | Yes No NA | Yes No NA |
| For above ground tanks (ground level or elevated/standpipe): |  |  |  |
| Is there #24-mesh screen? @ | Yes No NA | Yes No NA | Yes No NA |
| If not #24-mesh screen, what size mesh is the screen? |  |  |  |
| Does the tank have a vacuum/pressure relief valve or other mechanism to prevent tank damage? | Yes No NA | Yes No NA | Yes No NA |
| Is the screen on the inside of the vent pipe to discourage vandalism? | Yes No NA | Yes No NA | Yes No NA |
| Downturned vent: Is the vent at least 24“ above the roof? @ | Yes No NA | Yes No NA | Yes No NA |
| For non-downturned vents: Is there a solid cover down to the bottom of the vent screen? @ | Yes No NA | Yes No NA | Yes No NA |
| For non-downturned vents: Is the screen at least 8” above the roof surface? @ | Yes No NA | Yes No NA | Yes No NA |
| Below Ground Tanks (buried or partially buried) |  |  |  |
| Is air vent covered with #24-mesh screen? @ | Yes No NA | Yes No NA | Yes No NA |
| Is the screen on the inside of the vent pipe to discourage vandalism? | Yes No NA | Yes No NA | Yes No NA |
| Does the air vent terminate downward? @ | Yes No NA | Yes No NA | Yes No NA |
| Is the air vent at least 24” above the roof or ground surface (whichever is higher)? @ | Yes No NA | Yes No NA | Yes No NA |
| Comments about air vent: |  |  |  |
| Access Hatch |  |  |  |
| Are all hatch components accessible for inspection? @ | Yes No NA | Yes No NA | Yes No NA |
| For below ground tanks where the roof is completely buried, is the hatch raised at least 24” above ground level? @ | Yes No NA | Yes No NA | Yes No NA |
| For partially buried tanks where a roof is visible, is the hatch raised at least 24” above the roof? @ | Yes No NA | Yes No NA | Yes No NA |
| For above ground tanks (ground level or elevated) is the hatch raised at least 4“ above the roof? @ | Yes No NA | Yes No NA | Yes No NA |
| What is the height of the access hatch above roof or ground surface? | in | in | in |
| Does the hatch have a shoe box cover? @ | Yes No NA | Yes No NA | Yes No NA |
| Is the hatch cover tight and sealed with a rubber gasket? @ | Yes No NA | Yes No NA | Yes No NA |
| Is the hatch cover locked? @ | Yes No NA | Yes No NA | Yes No NA |
| Comments about access hatch: |  |  |  |
| Comments: |  |  |  |

# STORAGE TANKS

NA

| Complete for all tanks at ground water systems and consecutive systems Also complete for finished water tanks at surface water / GWUDI systems. (Includes indoor clearwells and contact tanks or other finished water tanks.) |  |  |  |
| --- | --- | --- | --- |
| Tank Name: |  |  |  |
| Tank ID (from PWS inventory, e.g., ST01): |  |  |  |
| Tank owner (if different than system owner): |  |  |  |
| Location (indoor or outdoor): |  |  |  |
| Date put into service |  |  |  |
| Tank Type Below ground (buried or partially buried) Ground level Elevated (pedestal or standpipe) |  |  |  |
| Tank is constructed of: Concrete Steel Fiberglass Other |  |  |  |
| What type of water is stored (GW systems only)? NA | Treated Raw | Treated Raw | Treated Raw |
| Storage Volume (gallons)? |  |  |  |
| Are there any approved WY DEQ Chapter 12 variances for this tank? If yes, describe what type of variance was approved. | Yes No | Yes No | Yes No |
| Is the site subject to flooding? @ | Yes No | Yes No | Yes No |
| Can the tank be isolated from the system? | Yes No | Yes No | Yes No |
| Is the water level indicator accurate? | Yes No | Yes No | Yes No |
| Does the tank have a mixer? | Yes No | Yes No | Yes No |
| Does the tank appear structurally sound? @ | Yes No | Yes No | Yes No |
| Does the foundation appear structurally sound? @ | Yes No NA | Yes No NA | Yes No NA |
| Are there unprotected openings in the tank (breaches, leaks, etc.)? @ | Yes No | Yes No | Yes No |
| Inspection and cleaning history |  |  |  |
| How often are the tank hatch, vent, and overflow visually inspected? |  |  |  |
| If the tank is more than 10 years old, was it cleaned and inspected within the last 10 years? @ | Yes No NA | Yes No NA | Yes No NA |
| When and how was the tank last cleaned and inspected? |  |  |  |
| Who performed the cleaning and inspection? |  |  |  |
| How was the tank disinfected after cleaning? (NA if diver used) |  |  |  |
| Surveyor able to view report and confirm date? | Yes No | Yes No | Yes No |
| If yes note major concerns and/or recommendations: |  |  |  |
| If Carcasses or other debris found in the tank: |  |  |  |
| Was EPA notified immediately? | Yes No | Yes No | Yes No |
| Was the entry point for the carcass or debris eliminated? | Yes No | Yes No | Yes No |
| Describe: |  |  |  |
| Overflow |  |  |  |
| Does the tank have an overflow separate from the vent? @ | Yes No NA | Yes No NA | Yes No NA |
| Is the overflow accessible for inspection? @ | Yes No NA | Yes No NA | Yes No NA |
| Overflow has a #24-mesh screen OR a duckbill valve OR a properly sealed flapper valve with screen of any size inside (EPA recommends a #24-mesh screen)? @ | Yes No NA | Yes No NA | Yes No NA |
| Does the overflow line terminate no less than 12 inches but no more than 24 inches above the ground surface? @ | Yes No NA | Yes No NA | Yes No NA |
| Does the overflow discharge over an inlet structure, splash plate, or engineered rip-rap? @ | Yes No NA | Yes No NA | Yes No NA |
| Is the discharge visible? | Yes No NA | Yes No NA | Yes No NA |
| Does the overflow have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? @ | Yes No NA | Yes No NA | Yes No NA |
| Comments about overflow: |  |  |  |
| Drain Line |  |  |  |
| Combined overflow and drain pipe? (If yes, skip drain questions) | Yes No NA | Yes No NA | Yes No NA |
| Is the drain accessible for inspection? @ | Yes No NA | Yes No NA | Yes No NA |
| Is there #24-mesh screen on the drain pipe? | Yes No NA | Yes No NA | Yes No NA |
| Does water accumulate in the drain discharge area? | Yes No NA | Yes No NA | Yes No NA |
| Does the drain pipe have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? @ | Yes No NA | Yes No NA | Yes No NA |
| Does the drain pipe terminate between 12 and 24 inches above a drainage area? | Yes No NA | Yes No NA | Yes No NA |
| Does the drain pipe terminate above an inlet structure, splash plate, or engineered rip-rap? | Yes No NA | Yes No NA | Yes No NA |
| Comments about drain: |  |  |  |
| Air Vent |  |  |  |
| Does the tank have a vent separate from the overflow? @ | Yes No NA | Yes No NA | Yes No NA |
| Is the vent accessible for inspection? @ | Yes No NA | Yes No NA | Yes No NA |
| For above ground tanks (ground level or elevated/standpipe): |  |  |  |
| Is there #24-mesh screen? @ | Yes No NA | Yes No NA | Yes No NA |
| If not #24-mesh screen, what size mesh is the screen? |  |  |  |
| Does the tank have a vacuum/pressure relief valve or other mechanism to prevent tank damage? | Yes No NA | Yes No NA | Yes No NA |
| Is the screen on the inside of the vent pipe to discourage vandalism? | Yes No NA | Yes No NA | Yes No NA |
| Downturned vent: Is the vent at least 24“ above the roof? @ | Yes No NA | Yes No NA | Yes No NA |
| For non-downturned vents: Is there a solid cover down to the bottom of the vent screen? @ | Yes No NA | Yes No NA | Yes No NA |
| For non-downturned vents: is the screen at least 8” above the roof surface? @ | Yes No NA | Yes No NA | Yes No NA |
| Below Ground Tanks (buried or partially buried) |  |  |  |
| Is air vent covered with #24-mesh screen? @ | Yes No NA | Yes No NA | Yes No NA |
| Is the screen on the inside of the vent pipe to discourage vandalism? | Yes No NA | Yes No NA | Yes No NA |
| Does the air vent terminate downward@ | Yes No NA | Yes No NA | Yes No NA |
| Is the air vent at least 24” above the roof or ground surface (whichever is higher)? @ | Yes No NA | Yes No NA | Yes No NA |
| Comments about air vent: |  |  |  |
| Access Hatch |  |  |  |
| Are all hatch components accessible for inspection? @ | Yes No NA | Yes No NA | Yes No NA |
| For below ground tanks where the roof is completely buried, is the hatch raised at least 24” above ground level? @ | Yes No NA | Yes No NA | Yes No NA |
| For partially buried tanks where a roof is visible, is the hatch raised at least 24” above the roof? @ | Yes No NA | Yes No NA | Yes No NA |
| For above ground tanks (ground level or elevated) is the hatch raised at least 4“ above the roof? @ | Yes No NA | Yes No NA | Yes No NA |
| What is the height of the access hatch above roof or ground surface? | in | in | in |
| Does the hatch have a shoe box cover? @ | Yes No NA | Yes No NA | Yes No NA |
| Is the hatch cover tight and sealed with a rubber gasket? @ | Yes No NA | Yes No NA | Yes No NA |
| Is the hatch cover locked? @ | Yes No NA | Yes No NA | Yes No NA |
| Comments about access hatch: |  |  |  |
| Comments: |  |  |  |

# DISTRIBUTION BOOSTER PUMP STATIONS

NA

| Total number of booster stations in the distribution system: Are there any new booster stations since the previous survey? Yes No Are there any booster stations the system has had problems with since the previous survey? Yes No Are there any booster stations where chlorine is added? Yes No Note to surveyor: If there are new or problem booster stations, or if there are booster stations where chlorine is added, inspect each of them, complete the sections below, and take photos of each station inspected. For booster stations where chlorine is added, add the chlorination as a treatment process under the “Water Treatment Data” section, in addition to filling out the booster pump station section below. If there are no new or problem booster stations, inspect at least one booster station as a representative of the entire system, complete a section below for each station inspected, and take photos of the station(s) inspected. |  |  |
| --- | --- | --- |
| Name/location of the pump station: How many pumps at the facility? Type/Make/Model/HP of pumps: | Incoming pressure (suction side) of booster station (psi): Outgoing pressure (discharge side) of booster station (psi): Estimated run time of booster pump(s) at time of visit (min): |  |
| Are booster pumps operated with Variable Frequency Drives (VFDs)? If Yes, make/model: Yes No Yes No NA Are the correct types of lubricants (NSF-60) used? Is the pump station subject to flooding? @ |  |  |
| Are pumps operable and in good condition? Is there a maintenance program in operation? Are spare pumps/parts available (specify)? Is emergency power available? |  |  |
| Name/location of the pump station: How many pumps at the facility? Type/Make/Model/HP of pumps: |  | Incoming pressure (suction side) of booster station (psi): Outgoing pressure (discharge side) of booster station (psi): Estimated run time of booster pump(s) at time of visit (min): |
| Are booster pumps operated with Variable Frequency Drives (VFDs)? If Yes, make/model: Yes No Yes No NA Are the correct types of lubricants (NSF-60) used? Is the pump station subject to flooding? @ |  |  |
| Are pumps operable and in good condition? Is there a maintenance program in operation? Are spare pumps/parts available? Is emergency power available? |  |  |
| Name/location of the pump station: How many pumps at the facility? Type/Make/Model/HP of pumps: |  | Incoming pressure (suction side) of booster station (psi): Outgoing pressure (discharge side) of booster station (psi): Estimated run time of booster pump(s) at time of visit (min): |
| Are booster pumps operated with Variable Frequency Drives (VFDs)? If Yes, make/model: Yes No Yes No NA Are the correct types of lubricants (NSF-60) used? Is the pump station subject to flooding? @ |  |  |
| Are pumps operable and in good condition? Is there a maintenance program in operation? Are spare pumps/parts available? Is emergency power available? |  |  |

# HYDROPNEUMATIC TANKS

(Fill out one section for each tank/set of tanks with a unique facility ID)

NA

| Type of Tanks Captive air bladder tank Pressure tank that uses an air compressor Retention or surge tank Number of tanks: Facility ID: Location, Description: Dates put into service: Is there an operable pressure gauge? Yes No Cut in pressure (psi): Cut out pressure (psi): Pump run time (min): Is there evidence of severe rust? @ Yes No Is there evidence of water leaks? @ Yes No Is there evidence of air leaks? @ Yes No Is there evidence of flooding (if in a vault)? @ NA Yes No Is there a pressure relief valve? Yes No Can tank(s) be by-passed for repair? Yes No For any tank that uses an air compressor, NA Yes No is the tank age older than the life expectancy? @ (Manufacturer and model number) Comments: | Type of Tanks Captive air bladder tank Pressure Tank that uses an air compressor Retention or surge tank Number of tanks: Facility ID: Location, Description: Dates put into service: Is there an operable pressure gauge? Yes No Cut in pressure (psi): Cut out pressure (psi): Pump run time (min): Is there evidence of severe rust? @ Yes No Is there evidence of water leaks? @ Yes No Is there evidence of air leaks? @ Yes No Is there evidence of flooding (if in a vault)? @ NA Yes No Is there a pressure relief valve? Yes No Can tank(s) be by-passed for repair? Yes No For any tank that uses an air compressor, NA Yes No is the tank age older than the life expectancy? @ (Manufacturer and model number) Comments: |
| --- | --- |

# DISTRIBUTION DATA

| Please provide a brief description of the distribution system, including source to use piping: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Is there asbestos pipe in the distribution system? Yes No If yes, what are the location and estimated linear feet of the asbestos pipe in the distribution system? Has all of the asbestos pipe been removed? Yes No NA If so, when was it removed? |  |  |  |  |
| Have lines broken due to freezing? Yes No Have lines broken due to traffic load? Yes No |  |  |  |  |
| Are lines properly disinfected after repairs are made? Yes No |  |  |  |  |
| Does the system provide fire protection (for example, fire hydrants located in distribution)? Yes No |  |  |  |  |
| According to the system representative, volume of water distributed per year and in the peak month: NI Annual volume distributed (MG/yr):; Peak month:; Volume distributed in peak month (MG). |
| For systems that provide water storage: NA Total number of days of storage (Summer)? Total number of days of storage (Winter)? |  |  |  |  |
| Is the storage capacity adequate to meet current needs? Yes No NI Is the storage capacity adequate to meet future needs? Yes No NI |  |  | Comments: |  |
| Are there any bulk water supply/fill stations attached to this system? Yes No Note to surveyor: if yes, check each facility, note its condition and provide photos |  |  |  |  |
| Station name (if applicable) | Location | Appropriate Air Gap or RPZ? |  | Comments |
|  |  | Air Gap RPZ Neither @ |  |  |
|  |  | Air Gap RPZ Neither @ |  |  |
|  |  | Air Gap RPZ Neither @ |  |  |
| Are there any air relief valves in vaults/pits located in the distribution system? Yes No Note to surveyor: If yes, inspect one representative ARV, note its condition and provide photos Are they regularly inspected and maintained? Yes No NA Do any have leaks and/or standing water that covers the discharge point? @ Yes No NA |  |  |  |  |
| Are there long dead end lines in excess of 500 feet in the distribution system? Yes No |  |  |  |  |
| Does the system have a flushing plan to ensure all fire hydrants and valves are exercised regularly? Yes No |  |  |  |  |
| How often does the system perform flushing operations in the distribution system? |  |  |  |  |
| Are distribution system (“as-built”) drawings maintained (e.g., revised to show replacement or repair?) Yes No |  |  |  |  |
| For systems that add a chemical disinfectant or receive disinfected water from a wholesaler: NA Yes No Is test equipment available for measuring the chlorine residual in the distribution system? Describe equipment: Are reagents up to date? Does the operator know how to properly measure chlorine residual? Measured chlorine residual distribution system location: Time of analysis: Indicate residual value measured at this distribution system location: By Surveyor: (mg/L) By PWS: (mg/L) Was free or total chlorine measured? It is recommended to maintain a minimum residual of 0.5 mg/L total or 0.2 mg/L free chlorine. |  |  |  |  |
| Distribution Pressure (NA may be checked for systems such as hand pump wells) NA |  |  |  |  |
| According to the system representative, is there at least 35 psi pressure in the distribution system at peak flow? Yes No |  |  |  |  |
| According to the system representative, is there at least 20 psi at all points in the system at all times? @ Yes No |  |  |  |  |
| How does the water system monitor distribution pressure? |  |  |  |  |
| Pressure measurement and location (if measured at the time of the survey): |  |  |  |  |
| Distribution water loss rate (%): |  |  |  |  |

# CROSS CONNECTION CONTROL

Yes No NA

Has the system conducted a service connections audit to determine if any high or severe hazard connections exist?

Does the system have a cross connection control and backflow prevention program in place?

Does each severe hazard connection have the appropriate reduced pressure backflow assembly installed at the meter/service connection and approved air gap (twice the size of the supply pipe diameter but always greater than one inch)? Describe each severe hazard connection and its location. @

Note: Severe hazard connections include radioactive materials processors, nuclear reactors, and sewage treatment plants/pump stations.

Does each high hazard connection in the treatment plant or distribution system have the appropriate air gap or reduced pressure backflow assembly installed? Describe each high hazard connection and its location. @

Note: High hazard connections include hospitals, medical/dental facilities, laboratories, mortuaries, large taxidermies, chemical suppliers/processing facilities, petroleum plants, food processing facilities, wastewater treatment plants, and docks, car washes, dry cleaners, direct connections to raw or non-potable water, and any service connection with an unapproved auxiliary supply.

Do trailers or mobile homes connected directly to the PWS via a yard hydrant have a residential dual check valve at each connection?

Are any frost-free hydrants that drain into the soil directly connected to this PWS?

Are there any leaking system components in the water system observed by the surveyor that are not previously noted? @

Explain where and what was leaking:

At Community PWS, do all low hazard connections have the appropriate dual check valve assemblies installed at the meter or service connection?

Note: Low hazard connections include mobile home parks, farms/dairies, ranches, and shopping centers.

For all systems with stock tanks or yard hydrants under the direct control of the system owner, do those connections have the indicated type of backflow prevention assemblies?

- Stock tanks – approved air gap or atmospheric vacuum breaker at the tank? @

- Threaded yard hydrants – vacuum breaker or double check valve assembly?

Does the water supplier have a record keeping program and management procedures to ensure:

- The installation and certification by test or inspection (as applicable) of all backflow preventers (BFPs) at new service connections

- The annual certification by a certified tester of all high-hazard BFPs at service connections.

SAFETY

General Safety

Yes No NA

Is the fire department familiar with the facilities and their contents?

Personnel Safety

Yes No NA

Are all personnel trained in proper handling of all utilized chemicals and materials?

Are adequate masks, protective clothing, and safety equipment provided?

Does the operator understand relevant Occupational Safety and Health Administration (OSHA) regulations (e.g., confined space, hazard communication, trenching/shoring, lock out/tag out)?

Chlorine Gas Safety NA

Yes No NA

Are there chlorine warnings posted on the outside of chlorine room doors?

- Do the doors open outward?

- Do they open to the exterior of the building?

- Are chlorine room doors equipped with crash bars?

Are there viewports in the interior wall and/or the doors of the chlorine room?

Is there a leak detector in the chlorine room with an audible alarm?

Are chlorine feed and storage areas isolated from other facilities?

Are chlorine areas adequately ventilated?

Are all chlorine cylinders adequately restrained?

Are self-contained breathing apparatus (SCBA) available for use in chlorine emergencies?

- Are they in good working condition?

- Are water system personnel adequately trained in the use and maintenance of the SCBA?

- Where are the SCBA stored?

Are chlorine leak kits available? Are all personnel trained in their proper use?

Chemical Safety NA

Yes No NA

Are oxidizers, corrosives, and flammables stored in separate areas and in closed, marked containers?

Are flammables stored in appropriate containers and cabinets away from combustion sources?

Is there adequate ventilation in the areas where solvents, aerosols, and chemical feeders are in use?

Are bulk storage areas physically isolated from treatment areas to prevent spills from entering the water system?

# MANAGEMENT DATA

Yes No NA

Are there rules governing new hookups to protect the integrity of this water system?

Are DEQ construction standards followed?

Is the treatment plant being properly operated to prevent inadequately treated water from being sent to the distribution system? @

Does the system have arrangements in place to assure prompt supply and repair service?

Does the system have a current operations and maintenance manual which describes all procedures, equipment, sampling schedules and inspection data?

Is there a schedule for routine preventative maintenance for all facilities and equipment?

Does the system (treatment plant, finished water storage) have security measures in place (fencing, locks, lighting, alarms, etc.)?

Does the system have an emergency response plan (ERP) – system does not need to show the surveyor the ERP --that includes: @

- Emergency contact phone numbers?

- Procedures to respond to a pressure loss/water outage?

- Procedures to respond to a water contamination incident?

- Is the ERP accessible to the operator on-site?

Is the system part of the state’s Water and Wastewater Agency Response Network (WARN)?

Have you evaluated possible impacts to your system from extreme weather events?

If yes, what was the outcome?

Have you evaluated your facilities to see if they are in the 100 and 500 year flood plains?

If yes, what was the outcome?

Does any of the system’s power comes from your own renewable energy sources? Yes No

% wind: % solar: % hydro:

For Community systems (including consecutives): NA

Yes No NA

Does the water system have an annual budget?

Is the rate structure for water customers based on metered water use?

Are procedures in place to handle delinquent accounts?

Are purchasing procedures in place for equipment, materials, chemicals, lab analysis, etc.?

List rates: Minimum ($): for gallons + ($) per 1,000 gallons thereafter Or, ($): (Flat Rate) Other (describe):

What percentage of your customer accounts are delinquent?

# MONITORING AND RECORDS

Revised Total Coliform Rule (RTCR) monitoring (all systems)

Yes No

Does the operator know how to collect and properly label samples for total coliform analysis? (Review operator sampling procedure at time of survey to confirm)

Does the operator know what to do in the event of a total coliform positive result? They will need to take 3 repeat samples under the RTCR utilizing the regular lab form: For an explanation go to the EPA Region 8 Drinking Water Online website (http://www.epa.gov/region8-waterops) - “click” on Revised Total Coliform Rule (RTCR) (under Regulations and Compliance) - “click” on Tech Tip: TC+ Follow Up (in green box) - Follow the 5 steps described in the Tech Tip for follow up sampling after a TC+ sample Are extra bottles available on site in case of need for repeat total coliform sampling?. Does the system have an RTCR sampling plan on file and available for the surveyor’s review (give date of plan)?.

Ask the operator - Is the system following their RTCR sampling plan? If No, explain any difficulties

If subject to the Ground Water Rule (GWR), does the operator know: NA

Yes No NA

Does the operator know when they have to collect a triggered GWR source sample? Within 24 hours of being notified of a routine total coliform positive sample result, they must collect one triggered source water sample for every routine total coliform positive sample at each active ground water source (e.g., three routine total coliform positive samples requires the operator to collect three source water samples from each ground water source).

They will need to submit:

- Source water sample results utilizing the triggered Ground Water Source Sampling Form located on the Drinking Water Online site (http://www.epa.gov/region8-waterops)?

Are extra bottles available on site in case of the need for GWR source sampling?

For Community and NTNC systems (including consecutives): NA

Yes No NA

Is there a Disinfection Byproducts Rule Monitoring Plan on-site available for the surveyor’s review?

If yes, does the plan have an exhibit representing the current distribution system layout? Does the operator feel that the current Total Trihalomethanes (TTHM) sample is at the oldest water age in the distribution system?

Does the system have a Lead & Copper Tap Sample Site Plan on site and available for the surveyor’s review? - Is the system following the tiering criteria in the rule?

- Does the system reach out to the LCR Manager when there are issues accessing sample sites?

For All Systems:

Yes No NA

Does the operator know the location of each sample tap that represents the entry point(s) to the distribution system? (sample location for Nitrates, RADs, IOCs, SOCs and VOCs) Include, in your photo document, a photo of each sample tap used by the operator to collect samples at the entry point(s) to the distribution system. Show in the photo or in the photo comments where the sample tap is located relative to other water system facilities that are identified on the system schematic.

Does the operator know how to properly label samples taken from the entry point(s) to the distribution system? Document the sample point code and sample point description for each entry point. The sample point code(s) and sample point description(s) are indicated on the system schematic with a star. This information is how compliance samples should be labeled and the lab’s chain of custody completed. (e.g., Sample Point Code and Sample Point Description, such as SP01/Treatment Plant Sampling Point).

Has the PWS completed the monitoring that is specified in the EPA-provided monitoring schedule so far for this calendar year?

Are copies of all monitoring results filed and readily accessible?

Is the operator familiar with the Drinking Water Online (http://www.epa.gov/region8-waterops) and Drinking Water Watch (https://sdwisr8.epa.gov/Region8DWWPUB/) websites created for their benefit?

| fieldName | Question in Survey Form | Message |
| --- | --- | --- |
| chkCertOpN | (Inventory) Certified Operator*? | No certified operator. Certified drinking water operators are essential to providing safe drinking water and protecting the public health of Wyoming public water systems. Regulations promulgated under the Safe Drinking Water Act require that public water systems be operated by qualified personnel. EPA Region 8 requires all community water systems and non-transient non-community water systems to have, or agree to obtain, a certified operator. To address this significant deficiency, submittal of a Wyoming certified operator certificate or other documentation will be required to demonstrate that the operator has achieved the appropriate level of certification. Alternatively, the system could employ a certified contract operator; documentation will be required to show the contractual agreement and the contract operator’s certification level. Information on certified Wyoming contract operators may be found at the following website: https://deq.state.wy.us/wqd/www/opcert/ContractOperator.aspx. |
| chkCSStdingWtrLk1 | (Consecutive Systems) Does standing water exist in any meter pits? Yes No If so, what is the source of the standing water? Leaks | Master meter vault contains standing water from leaking water system components*. (see photo #) The master meter vault at the connection to the [wholesaler] water system contained standing water caused by leaking water system components in the vault. This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. The components must be repaired to halt the leakage. |
| chkCSStdingWtrLk2 | (Consecutive Systems) Does standing water exist in any meter pits? Yes No If so, what is the source of the standing water? Leaks | Master meter vault contains standing water from leaking water system components*. (see photo #) The master meter vault at the connection to the [wholesaler] water system contained standing water caused by leaking water system components in the vault. This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. The components must be repaired to halt the leakage. |
| chkCSStdingWtrLk3 | (Consecutive Systems) Does standing water exist in any meter pits? Yes No If so, what is the source of the standing water? Leaks | Master meter vault contains standing water from leaking water system components*. (see photo #) The master meter vault at the connection to the [wholesaler] water system contained standing water caused by leaking water system components in the vault. This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. The components must be repaired to halt the leakage. |
| chkCSStdingWtrDtkn1 | (Consecutive Systems) Does standing water exist in any meter pits? Yes No If so, what is the source of the standing water? Don’t know | Master meter vault contains standing water from unknown origin*. (see photo #) The master meter vault at the connection to the [wholesaler] water system contained standing water caused by unknown source(s). This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. Since the [consecutive] is responsible for the maintenance of the master meter connection, the [consecutive] must identify the source of the standing water. If the source of the water is leakage from water system components, these must be repaired according to a schedule that you submit to the EPA. |
| chkCSStdingWtrDtkn2 | (Consecutive Systems) Does standing water exist in any meter pits? Yes No If so, what is the source of the standing water? Don’t know | Master meter vault contains standing water from unknown origin*. (see photo #) The master meter vault at the connection to the [wholesaler] water system contained standing water caused by unknown source(s). This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. Since the [consecutive] is responsible for the maintenance of the master meter connection, the [consecutive] must identify the source of the standing water. If the source of the water is leakage from water system components, these must be repaired according to a schedule that you submit to the EPA. |
| chkCSStdingWtrDtkn3 | (Consecutive Systems) Does standing water exist in any meter pits? Yes No If so, what is the source of the standing water? Don’t know | Master meter vault contains standing water from unknown origin*. (see photo #) The master meter vault at the connection to the [wholesaler] water system contained standing water caused by unknown source(s). This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. Since the [consecutive] is responsible for the maintenance of the master meter connection, the [consecutive] must identify the source of the standing water. If the source of the water is leakage from water system components, these must be repaired according to a schedule that you submit to the EPA. |
| chkTiteCapFilPortN | (Consecutive Systems) Is there a watertight cap on the (water system’s) fill port? | The water system’s fill port does not have a watertight cap. The cap on the water system’s fill port is not watertight. This could lead to the introduction of contamination into the distribution system. The cap must be repaired or replaced. |
| chk1WSStdingWtrLk | (Wholesale Systems) Does standing water exist in any meter pits for which the wholesale system is responsible? Yes No If so, what is the source of the standing water? Leaks | Master meter vault contains standing water from leaking water system components*. (see photo #) The master meter vault at the connection to the [consecutive] water system contained standing water caused by leaking water system components in the vault. This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. The components must be repaired to halt the leakage. |
| chk2WSStdingWtrLk | (Wholesale Systems) Does standing water exist in any meter pits for which the wholesale system is responsible? Yes No If so, what is the source of the standing water? Leaks | Master meter vault contains standing water from leaking water system components*. (see photo #) The master meter vault at the connection to the [consecutive] water system contained standing water caused by leaking water system components in the vault. This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. The components must be repaired to halt the leakage. |
| chk3WSStdingWtrLk | (Wholesale Systems) Does standing water exist in any meter pits for which the wholesale system is responsible? Yes No If so, what is the source of the standing water? Leaks | Master meter vault contains standing water from leaking water system components*. (see photo #) The master meter vault at the connection to the [consecutive] water system contained standing water caused by leaking water system components in the vault. This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. The components must be repaired to halt the leakage. |
| chk1WSStdingWtLkDK | (Wholesale Systems) Does standing water exist in any meter pits for which the wholesale system is responsible? Yes No If so, what is the source of the standing water? Don’t know | Master meter vault contains standing water from unknown origin*. (see photo #) The master meter vault at the connection to the [consecutive] water system contained standing water caused by unknown source(s). This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. Since the [wholesaler] is responsible for the maintenance of the master meter connection, the [wholesaler] must identify the source of the standing water. If the source of the water is leakage from water system components, these must be repaired according to a schedule that you submit to the EPA. |
| chk2WSStdingWtLkDK | (Wholesale Systems) Does standing water exist in any meter pits for which the wholesale system is responsible? Yes No If so, what is the source of the standing water? Don’t know | Master meter vault contains standing water from unknown origin*. (see photo #) The master meter vault at the connection to the [consecutive] water system contained standing water caused by unknown source(s). This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. Since the [wholesaler] is responsible for the maintenance of the master meter connection, the [wholesaler] must identify the source of the standing water. If the source of the water is leakage from water system components, these must be repaired according to a schedule that you submit to the EPA. |
| chk3WSStdingWtLkDK | (Wholesale Systems) Does standing water exist in any meter pits for which the wholesale system is responsible? Yes No If so, what is the source of the standing water? Don’t know | Master meter vault contains standing water from unknown origin*. (see photo #) The master meter vault at the connection to the [consecutive] water system contained standing water caused by unknown source(s). This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. Since the [wholesaler] is responsible for the maintenance of the master meter connection, the [wholesaler] must identify the source of the standing water. If the source of the water is leakage from water system components, these must be repaired according to a schedule that you submit to the EPA. |
| WL1ConsInactY | (Source Data – Wells) Does system want this well to be considered inactive? | Clarify Status of Groundwater Well and Perform Appropriate Monitoring, Physical Disconnection, or Abandonment*. During the sanitary survey, the EPA was notified that this well is considered inactive and there are no plans to use it for potable water. Please note that if you wish to keep the existing well physically connected as a backup source, you must monitor this well for compliance in the same way you would if the well was used on a regular basis. This well will also be inspected as part of the sanitary survey and you must address any significant deficiencies related to this well. If you wish this well to be considered inactive, it must be either plugged and abandoned, or physically disconnected from the system. This means the line from the well to the pumphouse or to the transmission line must be severed (section of piping removed) and properly capped, or the pump must be removed, or the power source to the well pump must be physically disconnected (e.g. wires removed). The well must also be valved off to keep stagnant water from entering the system. In order to correct this significant deficiency, please confirm whether this well is active or inactive. If this well is to be considered inactive, it must be physically disconnected or abandoned. Photos must be taken to document the inactive status of this well, and should be provided to EPA with your completed correction notice. |
| WL1VehicleProtectN | (Source Data – Wells) Adequately protected from vehicle damage? | Well not adequately protected from vehicle damage. (see photo #) The wellhead must be adequately protected to prevent damage due to vehicle operations. |
| WL1PitSumpPumpN | (Source Data – Wells) If the pit or vault is not watertight, is it completed with drainage or a sump pump for permanent or portable use? | Lack of drainage for well in pit or vault*. (see photo #) When a well is in a pit or vault that is not watertight, the pit or vault shall be constructed with proper drainage or an adequate permanent or portable pump that achieves proper drainage shall be provided. Adequate drainage means that the floor of the vault must be dry at all times and only the below-grade sump can retain a small amount of water between pumping events. |
| WL1SWDrainN | (Source Data – Wells) Does SW runoff drain away from the wellhead (including wells in pits or vaults)? | Well area subject to surface drainage. (see photo #) The wellhead is located in a low-lying area where surface water may drain toward the wellhead. The area surrounding the well must be recontoured, raised and sloped to drain surface water away from the wellhead. Permanent casing for the well must remain at least 18 inches above the natural ground surface. Drainage away from the well may also be accomplished by utilizing diversionary structures such as berms, walls, or ditches. |
| WL1CasTerm12InN | (Source Data – Wells) Does well casing terminate at least 12” above the concrete floor? | Insufficient well height*. (see photo #) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above the natural ground surface. |
| WL1CasTerm18InGrdN | (Source Data – Wells) Does the well casing terminate at least 18” above the natural ground surface? | Insufficient well height*. (see photo # ) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above natural ground surface. |
| WL1HolesinWellY | (Source Data – Wells) Any holes or openings observed in the well or its appurtenances? | Holes or openings observed in the well or its appurtenances*. (see photo # ) To prevent contamination of the well, all openings must be sealed and watertight. [describe what must be sealed]. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. |
| WL1SanSealN | (Source Data – Wells) Does the well have a sanitary seal with tightly bolted cap? (No) | Lack of a sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. |
| WL1SanSealUnk | (Source Data – Wells) Does the well have a sanitary seal with tightly bolted cap? (Unknown) | Unknown integrity of sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. The surveyor was unable to determine the integrity of the seal during the survey; photo documentation must be provided showing the seal (describe what is needed such as remove the cap, etc.). |
| WL1VentAbvCasN | (Source Data – Wells) Does the vent terminate at or above the top of the casing or pitless unit? | Well vent height improvement needed*. (see photo #) The height of the well vent must be at least as high as the well casing or pitless unit. |
| WL1VentFaceDwnN | (Source Data – Wells) Is vent facing downward? | Well vent position improvement needed*. (see photo #) The vent must terminate in a downturned position. |
| WL1Screen24MeshN | (Source Data – Wells) Vent screened with #24-mesh? | Well vent screening improvement needed*. (see photo #) The well vent must be screened with a #24-mesh corrosion-resistant screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| WL1DischargPipDwnrdN | (Source Data – Wells) Discharge Piping Termination- In a downward position? | Well air release-vacuum relief valve improvement needed. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate in a downturned position. The modified piping design must also maintain at least 8 inches above the floor. |
| WL1DischrgPip8InAbN | (Source Data – Wells) Discharge Piping Termination- At least 8” above the floor? | Insufficient height of well air release-vacuum relief valve. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate at least 8 inches above the floor. The modified piping design must still terminate in a downward position. |
| WL1DischrgPip24MshN | (Source Data – Wells) Discharge Piping Termination- Screened with #24-mesh? | Screening of well air release-vacuum relief valve improvement needed. (see photo #) For well pipes equipped with an air release-vacuum relief valve, the air release piping must be covered with a #24-mesh corrosion-resistant screen. |
| WL1PumpSubjFloodY | (Source Data – Wells) Is the external pump subject to flooding? | External pump on well subject to flooding*. Flood water could create a potential backflow problem if the system loses pressure and surface water is siphoned back into the well piping. The pump should be re-located or adequately protected from flooding. |
| WL1SrWTpGWN | Well lacks Ground Water Rule sample tap.* | As required under the Ground Water Rule, a raw water sample tap must be installed so that water samples can be collected directly from the water source to determine the quality of the groundwater supply before treatment. The sample tap must be installed prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| WL1TpPriPTN | Ground Water Rule sample tap must be relocated or reconfigured.* | As required under the Ground Water Rule, the raw water sample tap must represent water collected directly from the water source to determine the quality of the groundwater supply. The sample tap for the well must be relocated so that it is prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| WL2ConsInactY | (Source Data – Wells) Does system want this well to be considered inactive? | Clarify Status of Groundwater Well and Perform Appropriate Monitoring, Physical Disconnection, or Abandonment*. During the sanitary survey, the EPA was notified that this well is considered inactive and there are no plans to use it for potable water. Please note that if you wish to keep the existing well physically connected as a backup source, you must monitor this well for compliance in the same way you would if the well was used on a regular basis. This well will also be inspected as part of the sanitary survey and you must address any significant deficiencies related to this well. If you wish this well to be considered inactive, it must be either plugged and abandoned, or physically disconnected from the system. This means the line from the well to the pumphouse or to the transmission line must be severed (section of piping removed) and properly capped, or the pump must be removed, or the power source to the well pump must be physically disconnected (e.g. wires removed). The well must also be valved off to keep stagnant water from entering the system. In order to correct this significant deficiency, please confirm whether this well is active or inactive. If this well is to be considered inactive, it must be physically disconnected or abandoned. Photos must be taken to document the inactive status of this well, and should be provided to EPA with your completed correction notice. |
| WL2VehicleProtectN | (Source Data – Wells) Adequately protected from vehicle damage? | Well not adequately protected from vehicle damage. (see photo #) The wellhead must be adequately protected to prevent damage due to vehicle operations. |
| WL2PitSumpPumpN | (Source Data – Wells) If the pit or vault is not watertight, is it completed with drainage or a sump pump for permanent or portable use? | Lack of drainage for well in pit or vault*. (see photo #) When a well is in a pit or vault that is not watertight, the pit or vault shall be constructed with proper drainage or an adequate permanent or portable pump that achieves proper drainage shall be provided. Adequate drainage means that the floor of the vault must be dry at all times and only the below-grade sump can retain a small amount of water between pumping events. |
| WL2SWDrainN | (Source Data – Wells) Does SW runoff drain away from the wellhead (including wells in pits or vaults)? | Well area subject to surface drainage. (see photo #) The wellhead is located in a low-lying area where surface water may drain toward the wellhead. The area surrounding the well must be recontoured, raised and sloped to drain surface water away from the wellhead. Permanent casing for the well must remain at least 18 inches above the natural ground surface. Drainage away from the well may also be accomplished by utilizing diversionary structures such as berms, walls, or ditches. |
| WL2CasTerm12InN | (Source Data – Wells) Does well casing terminate at least 12” above the concrete floor? | Insufficient well height*. (see photo #) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above the natural ground surface. |
| WL2CasTerm18InGrdN | (Source Data – Wells) Does the well casing terminate at least 18” above the natural ground surface? | Insufficient well height*. (see photo # ) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above natural ground surface. |
| WL2HolesinWellY | (Source Data – Wells) Any holes or openings observed in the well or its appurtenances? | Holes or openings observed in the well or its appurtenances*. (see photo # ) To prevent contamination of the well, all openings must be sealed and watertight. [describe what must be sealed]. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. |
| WL2SanSealN | (Source Data – Wells) Does the well have a sanitary seal? | Lack of a sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. |
| WL2SanSealUnk | (Source Data – Wells) Does the well have a sanitary seal with tightly bolted cap? (Unknown) | Unknown integrity of sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. The surveyor was unable to determine the integrity of the seal during the survey; photo documentation must be provided showing the seal (describe what is needed such as remove the cap, etc.). |
| WL2VentAbvCasN | (Source Data – Wells) Does the vent terminate at or above the top of the casing or pitless unit? | Well vent height improvement needed*. (see photo #) The height of the well vent must be at least as high as the well casing or pitless unit. |
| WL2VentFaceDwnN | (Source Data – Wells) Is vent facing downward? | Well vent position improvement needed*. (see photo #) The vent must terminate in a downturned position. |
| WL2Screen24MeshN | (Source Data – Wells) Vent screened with #24-mesh? | Well vent screening improvement needed*. (see photo #) The well vent must be screened with a #24-mesh corrosion-resistant screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| WL2DischargPipDwnrdN | (Source Data – Wells) Discharge Piping Termination- In a downward position? | Well air release-vacuum relief valve improvement needed. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate in a downturned position. The modified piping design must also maintain at least 8 inches above the floor. |
| WL2DischrgPip8InAbN | (Source Data – Wells) Discharge Piping Termination- At least 8” above the floor? | Insufficient height of well air release-vacuum relief valve. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate at least 8 inches above the floor. The modified piping design must still terminate in a downward position. |
| WL2DischrgPip24MshN | (Source Data – Wells) Discharge Piping Termination- Screened with #24-mesh? | Screening of well air release-vacuum relief valve improvement needed. (see photo #) For well pipes equipped with an air release-vacuum relief valve, the air release piping must be covered with a #24-mesh corrosion-resistant screen. |
| WL2PumpSubjFloodY | (Source Data – Wells) Is the external pump subject to flooding? | External pump on well subject to flooding*. Flood water could create a potential backflow problem if the system loses pressure and surface water is siphoned back into the well piping. The pump should be re-located or adequately protected from flooding. |
| WL2SrWTpGWN | Well lacks Ground Water Rule sample tap.* | As required under the Ground Water Rule, a raw water sample tap must be installed so that water samples can be collected directly from the water source to determine the quality of the groundwater supply before treatment. The sample tap must be installed prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| WL2TpPriPTN | Ground Water Rule sample tap must be relocated or reconfigured.* | As required under the Ground Water Rule, the raw water sample tap must represent water collected directly from the water source to determine the quality of the groundwater supply. The sample tap for the well must be relocated so that it is prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| WL3ConsInactY | (Source Data – Wells) Does system want this well to be considered inactive? | Clarify Status of Groundwater Well and Perform Appropriate Monitoring, Physical Disconnection, or Abandonment*. During the sanitary survey, the EPA was notified that this well is considered inactive and there are no plans to use it for potable water. Please note that if you wish to keep the existing well physically connected as a backup source, you must monitor this well for compliance in the same way you would if the well was used on a regular basis. This well will also be inspected as part of the sanitary survey and you must address any significant deficiencies related to this well. If you wish this well to be considered inactive, it must be either plugged and abandoned, or physically disconnected from the system. This means the line from the well to the pumphouse or to the transmission line must be severed (section of piping removed) and properly capped, or the pump must be removed, or the power source to the well pump must be physically disconnected (e.g. wires removed). The well must also be valved off to keep stagnant water from entering the system. In order to correct this significant deficiency, please confirm whether this well is active or inactive. If this well is to be considered inactive, it must be physically disconnected or abandoned. Photos must be taken to document the inactive status of this well, and should be provided to EPA with your completed correction notice. |
| WL3VehicleProtectN | (Source Data – Wells) Adequately protected from vehicle damage? | Well not adequately protected from vehicle damage. (see photo #) The wellhead must be adequately protected to prevent damage due to vehicle operations. |
| WL3PitSumpPumpN | (Source Data – Wells) If the pit or vault is not watertight, is it completed with drainage or a sump pump for permanent or portable use? | Lack of drainage for well in pit or vault*. (see photo #) When a well is in a pit or vault that is not watertight, the pit or vault shall be constructed with proper drainage or an adequate permanent or portable pump that achieves proper drainage shall be provided. Adequate drainage means that the floor of the vault must be dry at all times and only the below-grade sump can retain a small amount of water between pumping events. |
| WL3SWDrainN | (Source Data – Wells) Does SW runoff drain away from the wellhead (including wells in pits or vaults)? | Well area subject to surface drainage. (see photo #) The wellhead is located in a low-lying area where surface water may drain toward the wellhead. The area surrounding the well must be recontoured, raised and sloped to drain surface water away from the wellhead. Permanent casing for the well must remain at least 18 inches above the natural ground surface. Drainage away from the well may also be accomplished by utilizing diversionary structures such as berms, walls, or ditches. |
| WL3CasTerm12InN | (Source Data – Wells) Does well casing terminate at least 12” above the concrete floor? | Insufficient well height*. (see photo #) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above the natural ground surface. |
| WL3CasTerm18InGrdN | (Source Data – Wells) Does the well casing terminate at least 18” above the natural ground surface? | Insufficient well height*. (see photo # ) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above natural ground surface. |
| WL3HolesinWellY | (Source Data – Wells) Any holes or openings observed in the well or its appurtenances? | Holes or openings observed in the well or its appurtenances*. (see photo # ) To prevent contamination of the well, all openings must be sealed and watertight. [describe what must be sealed]. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. |
| WL3SanSealN | (Source Data – Wells) Does the well have a sanitary seal? | Lack of a sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. |
| WL3SanSealUnk | (Source Data – Wells) Does the well have a sanitary seal with tightly bolted cap? (Unknown) | Unknown integrity of sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. The surveyor was unable to determine the integrity of the seal during the survey; photo documentation must be provided showing the seal (describe what is needed such as remove the cap, etc.). |
| WL3VentAbvCasN | (Source Data – Wells) Does the vent terminate at or above the top of the casing or pitless unit? | Well vent height improvement needed*. (see photo #) The height of the well vent must be at least as high as the well casing or pitless unit. |
| WL3VentFaceDwnN | (Source Data – Wells) Is vent facing downward? | Well vent position improvement needed*. (see photo #) The vent must terminate in a downturned position. |
| WL3Screen24MeshN | (Source Data – Wells) Vent screened with #24-mesh? | Well vent screening improvement needed*. (see photo #) The well vent must be screened with a #24-mesh corrosion-resistant screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| WL3DischargPipDwnrdN | (Source Data – Wells) Discharge Piping Termination- In a downward position? | Well air release-vacuum relief valve improvement needed. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate in a downturned position. The modified piping design must also maintain at least 8 inches above the floor. |
| WL3DischrgPip8InAbN | (Source Data – Wells) Discharge Piping Termination- At least 8” above the floor? | Insufficient height of well air release-vacuum relief valve. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate at least 8 inches above the floor. The modified piping design must still terminate in a downward position. |
| WL3DischrgPip24MshN | (Source Data – Wells) Discharge Piping Termination- Screened with #24-mesh? | Screening of well air release-vacuum relief valve improvement needed. (see photo #) For well pipes equipped with an air release-vacuum relief valve, the air release piping must be covered with a #24-mesh corrosion-resistant screen. |
| WL3PumpSubjFloodY | (Source Data – Wells) Is the external pump subject to flooding? | External pump on well subject to flooding*. Flood water could create a potential backflow problem if the system loses pressure and surface water is siphoned back into the well piping. The pump should be re-located or adequately protected from flooding. |
| WL3SrWTpGWN | Well lacks Ground Water Rule sample tap.* | As required under the Ground Water Rule, a raw water sample tap must be installed so that water samples can be collected directly from the water source to determine the quality of the groundwater supply before treatment. The sample tap must be installed prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| WL3TpPriPTN | Ground Water Rule sample tap must be relocated or reconfigured.* | As required under the Ground Water Rule, the raw water sample tap must represent water collected directly from the water source to determine the quality of the groundwater supply. The sample tap for the well must be relocated so that it is prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| WL4ConsInactY | (Source Data – Wells) Does system want this well to be considered inactive? | Clarify Status of Groundwater Well and Perform Appropriate Monitoring, Physical Disconnection, or Abandonment*. During the sanitary survey, the EPA was notified that this well is considered inactive and there are no plans to use it for potable water. Please note that if you wish to keep the existing well physically connected as a backup source, you must monitor this well for compliance in the same way you would if the well was used on a regular basis. This well will also be inspected as part of the sanitary survey and you must address any significant deficiencies related to this well. If you wish this well to be considered inactive, it must be either plugged and abandoned, or physically disconnected from the system. This means the line from the well to the pumphouse or to the transmission line must be severed (section of piping removed) and properly capped, or the pump must be removed, or the power source to the well pump must be physically disconnected (e.g. wires removed). The well must also be valved off to keep stagnant water from entering the system. In order to correct this significant deficiency, please confirm whether this well is active or inactive. If this well is to be considered inactive, it must be physically disconnected or abandoned. Photos must be taken to document the inactive status of this well, and should be provided to EPA with your completed correction notice. |
| WL4PitSumpPumpN | (Source Data – Wells) If the pit or vault is not watertight, is it completed with drainage or a sump pump for permanent or portable use? | Lack of drainage for well in pit or vault*. (see photo #) When a well is in a pit or vault that is not watertight, the pit or vault shall be constructed with proper drainage or an adequate permanent or portable pump that achieves proper drainage shall be provided. Adequate drainage means that the floor of the vault must be dry at all times and only the below-grade sump can retain a small amount of water between pumping events. |
| WL4SWDrainN | (Source Data – Wells) Does SW runoff drain away from the wellhead (including wells in pits or vaults)? | Well area subject to surface drainage. (see photo #) The wellhead is located in a low-lying area where surface water may drain toward the wellhead. The area surrounding the well must be recontoured, raised and sloped to drain surface water away from the wellhead. Permanent casing for the well must remain at least 18 inches above the natural ground surface. Drainage away from the well may also be accomplished by utilizing diversionary structures such as berms, walls, or ditches. |
| WL4CasTerm12InN | (Source Data – Wells) Does well casing terminate at least 12” above the concrete floor? | Insufficient well height*. (see photo #) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above the natural ground surface. |
| WL4CasTerm18InGrdN | (Source Data – Wells) Does the well casing terminate at least 18” above the natural ground surface? | Insufficient well height*. (see photo # ) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above natural ground surface. |
| WL4HolesinWellY | (Source Data – Wells) Any holes or openings observed in the well or its appurtenances? | Holes or openings observed in the well or its appurtenances*. (see photo # ) To prevent contamination of the well, all openings must be sealed and watertight. [describe what must be sealed]. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. |
| WL4SanSealN | (Source Data – Wells) Does the well have a sanitary seal? | Lack of a sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. |
| WL4SanSealUnk | (Source Data – Wells) Does the well have a sanitary seal with tightly bolted cap? (Unknown) | Unknown integrity of sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. The surveyor was unable to determine the integrity of the seal during the survey; photo documentation must be provided showing the seal (describe what is needed such as remove the cap, etc.). |
| WL4VentAbvCasN | (Source Data – Wells) Does the vent terminate at or above the top of the casing or pitless unit? | Well vent height improvement needed*. (see photo #) The height of the well vent must be at least as high as the well casing or pitless unit. |
| WL4VentFaceDwnN | (Source Data – Wells) Is vent facing downward? | Well vent position improvement needed*. (see photo #) The vent must terminate in a downturned position. |
| WL4Screen24MeshN | (Source Data – Wells) Vent screened with #24-mesh? | Well vent screening improvement needed*. (see photo #) The well vent must be screened with a #24-mesh corrosion-resistant screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| WL4DischargPipDwnrdN | (Source Data – Wells) Discharge Piping Termination- In a downward position? | Well air release-vacuum relief valve improvement needed. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate in a downturned position. The modified piping design must also maintain at least 8 inches above the floor. |
| WL4DischrgPip8InAbN | (Source Data – Wells) Discharge Piping Termination- At least 8” above the floor? | Insufficient height of well air release-vacuum relief valve. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate at least 8 inches above the floor. The modified piping design must still terminate in a downward position. |
| WL4DischrgPip24MshN | (Source Data – Wells) Discharge Piping Termination- Screened with #24-mesh? | Screening of well air release-vacuum relief valve improvement needed. (see photo #) For well pipes equipped with an air release-vacuum relief valve, the air release piping must be covered with a #24-mesh corrosion-resistant screen. |
| WL4PumpSubjFloodY | (Source Data – Wells) Is the external pump subject to flooding? | External pump on well subject to flooding*. Flood water could create a potential backflow problem if the system loses pressure and surface water is siphoned back into the well piping. The pump should be re-located or adequately protected from flooding. |
| WL4SrWTpGWN | Well lacks Ground Water Rule sample tap.* | As required under the Ground Water Rule, a raw water sample tap must be installed so that water samples can be collected directly from the water source to determine the quality of the groundwater supply before treatment. The sample tap must be installed prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| WL4TpPriPTN | Ground Water Rule sample tap must be relocated or reconfigured.* | As required under the Ground Water Rule, the raw water sample tap must represent water collected directly from the water source to determine the quality of the groundwater supply. The sample tap for the well must be relocated so that it is prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| WL5ConsInactY | (Source Data – Wells) Does system want this well to be considered inactive? | Clarify Status of Groundwater Well and Perform Appropriate Monitoring, Physical Disconnection, or Abandonment*. During the sanitary survey, the EPA was notified that this well is considered inactive and there are no plans to use it for potable water. Please note that if you wish to keep the existing well physically connected as a backup source, you must monitor this well for compliance in the same way you would if the well was used on a regular basis. This well will also be inspected as part of the sanitary survey and you must address any significant deficiencies related to this well. If you wish this well to be considered inactive, it must be either plugged and abandoned, or physically disconnected from the system. This means the line from the well to the pumphouse or to the transmission line must be severed (section of piping removed) and properly capped, or the pump must be removed, or the power source to the well pump must be physically disconnected (e.g. wires removed). The well must also be valved off to keep stagnant water from entering the system. In order to correct this significant deficiency, please confirm whether this well is active or inactive. If this well is to be considered inactive, it must be physically disconnected or abandoned. Photos must be taken to document the inactive status of this well, and should be provided to EPA with your completed correction notice. |
| WL5VehicleProtectN | (Source Data – Wells) Adequately protected from vehicle damage? | Well not adequately protected from vehicle damage. (see photo #) The wellhead must be adequately protected to prevent damage due to vehicle operations. |
| WL5PitSumpPumpN | (Source Data – Wells) If the pit or vault is not watertight, is it completed with drainage or a sump pump for permanent or portable use? | Lack of drainage for well in pit or vault*. (see photo #) When a well is in a pit or vault that is not watertight, the pit or vault shall be constructed with proper drainage or an adequate permanent or portable pump that achieves proper drainage shall be provided. Adequate drainage means that the floor of the vault must be dry at all times and only the below-grade sump can retain a small amount of water between pumping events. |
| WL5SWDrainN | (Source Data – Wells) Does SW runoff drain away from the wellhead (including wells in pits or vaults)? | Well area subject to surface drainage. (see photo #) The wellhead is located in a low-lying area where surface water may drain toward the wellhead. The area surrounding the well must be recontoured, raised and sloped to drain surface water away from the wellhead. Permanent casing for the well must remain at least 18 inches above the natural ground surface. Drainage away from the well may also be accomplished by utilizing diversionary structures such as berms, walls, or ditches. |
| WL5CasTerm12InN | (Source Data – Wells) Does well casing terminate at least 12” above the concrete floor? | Insufficient well height*. (see photo #) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above the natural ground surface. |
| WL5CasTerm18InGrdN | (Source Data – Wells) Does the well casing terminate at least 18” above the natural ground surface? | Insufficient well height*. (see photo # ) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above natural ground surface. |
| WL5HolesinWellY | (Source Data – Wells) Any holes or openings observed in the well or its appurtenances? | Holes or openings observed in the well or its appurtenances*. (see photo # ) To prevent contamination of the well, all openings must be sealed and watertight. [describe what must be sealed]. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. |
| WL5SanSealN | (Source Data – Wells) Does the well have a sanitary seal? | Lack of a sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. |
| WL5SanSealUnk | (Source Data – Wells) Does the well have a sanitary seal with tightly bolted cap? (Unknown) | Unknown integrity of sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. The surveyor was unable to determine the integrity of the seal during the survey; photo documentation must be provided showing the seal (describe what is needed such as remove the cap, etc.). |
| WL5VentAbvCasN | (Source Data – Wells) Does the vent terminate at or above the top of the casing or pitless unit? | Well vent height improvement needed*. (see photo #) The height of the well vent must be at least as high as the well casing or pitless unit. |
| WL5VentFaceDwnN | (Source Data – Wells) Is vent facing downward? | Well vent position improvement needed*. (see photo #) The vent must terminate in a downturned position. |
| WL5Screen24MeshN | (Source Data – Wells) Vent screened with #24-mesh? | Well vent screening improvement needed*. (see photo #) The well vent must be screened with a #24-mesh corrosion-resistant screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| WL5DischargPipDwnrdN | (Source Data – Wells) Discharge Piping Termination- In a downward position? | Well air release-vacuum relief valve improvement needed. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate in a downturned position. The modified piping design must also maintain at least 8 inches above the floor. |
| WL5DischrgPip8InAbN | (Source Data – Wells) Discharge Piping Termination- At least 8” above the floor? | Insufficient height of well air release-vacuum relief valve. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate at least 8 inches above the floor. The modified piping design must still terminate in a downward position. |
| WL5DischrgPip24MshN | (Source Data – Wells) Discharge Piping Termination- Screened with #24-mesh? | Screening of well air release-vacuum relief valve improvement needed. (see photo #) For well pipes equipped with an air release-vacuum relief valve, the air release piping must be covered with a #24-mesh corrosion-resistant screen. |
| WL5PumpSubjFloodY | (Source Data – Wells) Is the external pump subject to flooding? | External pump on well subject to flooding*. Flood water could create a potential backflow problem if the system loses pressure and surface water is siphoned back into the well piping. The pump should be re-located or adequately protected from flooding. |
| WL5SrWTpGWN | Well lacks Ground Water Rule sample tap.* | As required under the Ground Water Rule, a raw water sample tap must be installed so that water samples can be collected directly from the water source to determine the quality of the groundwater supply before treatment. The sample tap must be installed prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| WL5TpPriPTN | Ground Water Rule sample tap must be relocated or reconfigured.* | As required under the Ground Water Rule, the raw water sample tap must represent water collected directly from the water source to determine the quality of the groundwater supply. The sample tap for the well must be relocated so that it is prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| WL6ConsInactY | (Source Data – Wells) Does system want this well to be considered inactive? | Clarify Status of Groundwater Well and Perform Appropriate Monitoring, Physical Disconnection, or Abandonment*. During the sanitary survey, the EPA was notified that this well is considered inactive and there are no plans to use it for potable water. Please note that if you wish to keep the existing well physically connected as a backup source, you must monitor this well for compliance in the same way you would if the well was used on a regular basis. This well will also be inspected as part of the sanitary survey and you must address any significant deficiencies related to this well. If you wish this well to be considered inactive, it must be either plugged and abandoned, or physically disconnected from the system. This means the line from the well to the pumphouse or to the transmission line must be severed (section of piping removed) and properly capped, or the pump must be removed, or the power source to the well pump must be physically disconnected (e.g. wires removed). The well must also be valved off to keep stagnant water from entering the system. In order to correct this significant deficiency, please confirm whether this well is active or inactive. If this well is to be considered inactive, it must be physically disconnected or abandoned. Photos must be taken to document the inactive status of this well, and should be provided to EPA with your completed correction notice. |
| WL6VehicleProtectN | (Source Data – Wells) Adequately protected from vehicle damage? | Well not adequately protected from vehicle damage. (see photo #) The wellhead must be adequately protected to prevent damage due to vehicle operations. |
| WL6PitSumpPumpN | (Source Data – Wells) If the pit or vault is not watertight, is it completed with drainage or a sump pump for permanent or portable use? | Lack of drainage for well in pit or vault*. (see photo #) When a well is in a pit or vault that is not watertight, the pit or vault shall be constructed with proper drainage or an adequate permanent or portable pump that achieves proper drainage shall be provided. Adequate drainage means that the floor of the vault must be dry at all times and only the below-grade sump can retain a small amount of water between pumping events. |
| WL6SWDrainN | (Source Data – Wells) Does SW runoff drain away from the wellhead (including wells in pits or vaults)? | Well area subject to surface drainage. (see photo #) The wellhead is located in a low-lying area where surface water may drain toward the wellhead. The area surrounding the well must be recontoured, raised and sloped to drain surface water away from the wellhead. Permanent casing for the well must remain at least 18 inches above the natural ground surface. Drainage away from the well may also be accomplished by utilizing diversionary structures such as berms, walls, or ditches. |
| WL6CasTerm12InN | (Source Data – Wells) Does well casing terminate at least 12” above the concrete floor? | Insufficient well height*. (see photo #) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above the natural ground surface. |
| WL6CasTerm18InGrdN | (Source Data – Wells) Does the well casing terminate at least 18” above the natural ground surface? | Insufficient well height*. (see photo # ) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above natural ground surface. |
| WL6HolesinWellY | (Source Data – Wells) Any holes or openings observed in the well or its appurtenances? | Holes or openings observed in the well or its appurtenances*. (see photo # ) To prevent contamination of the well, all openings must be sealed and watertight. [describe what must be sealed]. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. |
| WL6SanSealN | (Source Data – Wells) Does the well have a sanitary seal? | Lack of a sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. |
| WL6SanSealUnk | (Source Data – Wells) Does the well have a sanitary seal with tightly bolted cap? (Unknown) | Unknown integrity of sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. The surveyor was unable to determine the integrity of the seal during the survey; photo documentation must be provided showing the seal (describe what is needed such as remove the cap, etc.). |
| WL6VentAbvCasN | (Source Data – Wells) Does the vent terminate at or above the top of the casing or pitless unit? | Well vent height improvement needed*. (see photo #) The height of the well vent must be at least as high as the well casing or pitless unit. |
| WL6VentFaceDwnN | (Source Data – Wells) Is vent facing downward? | Well vent position improvement needed*. (see photo #) The vent must terminate in a downturned position. |
| WL6Screen24MeshN | (Source Data – Wells) Vent screened with #24-mesh? | Well vent screening improvement needed*. (see photo #) The well vent must be screened with a #24-mesh corrosion-resistant screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| WL6DischargPipDwnrdN | (Source Data – Wells) Discharge Piping Termination- In a downward position? | Well air release-vacuum relief valve improvement needed. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate in a downturned position. The modified piping design must also maintain at least 8 inches above the floor. |
| WL6DischrgPip8InAbN | (Source Data – Wells) Discharge Piping Termination- At least 8” above the floor? | Insufficient height of well air release-vacuum relief valve. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate at least 8 inches above the floor. The modified piping design must still terminate in a downward position. |
| WL6DischrgPip24MshN | (Source Data – Wells) Discharge Piping Termination- Screened with #24-mesh? | Screening of well air release-vacuum relief valve improvement needed. (see photo #) For well pipes equipped with an air release-vacuum relief valve, the air release piping must be covered with a #24-mesh corrosion-resistant screen. |
| WL6PumpSubjFloodY | (Source Data – Wells) Is the external pump subject to flooding? | External pump on well subject to flooding*. Flood water could create a potential backflow problem if the system loses pressure and surface water is siphoned back into the well piping. The pump should be re-located or adequately protected from flooding. |
| WL6SrWTpGWN | Well lacks Ground Water Rule sample tap.* | As required under the Ground Water Rule, a raw water sample tap must be installed so that water samples can be collected directly from the water source to determine the quality of the groundwater supply before treatment. The sample tap must be installed prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| WL6TpPriPTN | Ground Water Rule sample tap must be relocated or reconfigured.* | As required under the Ground Water Rule, the raw water sample tap must represent water collected directly from the water source to determine the quality of the groundwater supply. The sample tap for the well must be relocated so that it is prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| sourceOPolutnNrWlY | (Source Data – Wells) Are there any sources of pollution near the wells which could impact water quality? | Source of possible contamination in immediate area of well. (see photo # ) In the vicinity of the well there is [describe sources of pollution] that can potentially impact the water quality. (Describe remedy) |
| srce456OPolutnNrWlY | (Source Data – Wells) Are there any sources of pollution near the wells which could impact water quality? | Source of possible contamination in immediate area of well. (see photo # ) In the vicinity of the well there is [describe sources of pollution] that can potentially impact the water quality. (Describe remedy) |
| WLone2or3animdropY | (Source Data – Wells) Mice or other animals and their droppings in immediate area? | Mice or other animals and their droppings in immediate area of the well (in well house, vault, or pit). (see photo # ) The mice or other animals and their droppings must be removed. Please refer to the Center for Disease Control (CDC) website regarding how to properly clean up this area to prevent contracting the Hantavirus pulmonary syndrome: http://www.cdc.gov/ncidod/diseases/hanta/hps/noframes/prevent3.htm |
| WLfour5or6animdropY | (Source Data – Wells) Mice or other animals and their droppings in immediate area? | Mice or other animals and their droppings in immediate area of the well (in well house, vault, or pit). (see photo # ) The mice or other animals and their droppings must be removed. Please refer to the Center for Disease Control (CDC) website regarding how to properly clean up this area to prevent contracting the Hantavirus pulmonary syndrome: http://www.cdc.gov/ncidod/diseases/hanta/hps/noframes/prevent3.htm |
| SprSrcFencedN | (Source Data Springs) Are the spring collection area and spring box fenced to keep animals away? | Spring collection area and collection chamber/box not fenced to keep large animals away. (see photo #) The spring collection area and collection chamber/box must be enclosed by a fence to prevent stock and large wildlife from entering the spring area. |
| properShoeBxLidN | (Source Data Springs) Proper shoe box lid? | Spring collection chamber hatch/entry improvement needed*. (see photo #) The cover must overlap the framed opening and extend down around the frame at least two inches. |
| RubberGasketOnLidN | (Source Data Springs) Rubber gasket on the lid? | Spring hatch/entry improvement needed*. (see photo # ) Spring hatches must be fitted with a solid, watertight cover with a rubber gasket. |
| AdequateAirVnt24MN | (Source Data Springs) Air vents screened with #24-mesh? | Spring air vent improvement needed*. (see photo #) The air vent must be screened with a #24-mesh corrosion-resistant screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| SprgHatchLockedN | (Source Data Springs) Is the hatch locked? | Spring hatch/entry not locked. (see photo #) Spring hatch covers must have a locking device. |
| spgScreenedOverFN | (Source Data Springs) Overflow screened with #24-mesh screen? | Spring collection chamber overflow screening improvement needed*. (see photo #) The overflow pipe must have a #24-mesh screen on the exterior discharge ends to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The modified overflow design must also still freefall at least 12 inches above ground. |
| SprOvrflFreeFall12N | (Source Data Springs) Does overflow have a free fall of at least 12 inches? | Spring collection chamber overflow improvement needed*. (see photo #) The overflow pipe must freefall at least 12 inches above ground. The modified overflow must also maintain a #24-mesh screen on the exterior discharge end. |
| sprCollChmbrWtrTiteN | (Source Data Springs) Is the spring collection chamber watertight to prevent inflow of unwanted surface water? | Spring collection chamber not watertight*. (see photo #) The chamber must be watertight to prevent inflow of unwanted surface water. |
| srcPmpSubjToFloodY | (Source Data Springs) Is the pump station subject to flooding? | External pump on spring subject to flooding*. Flood water could create a potential backflow problem if the system loses pressure and surface water is siphoned back into the spring transmission line. The pump should be re-located or adequately protected from flooding. |
| sprPropShoeBxLidN | (Source Data Springs) (Spring collection or distribution system hatches / manholes) Proper shoe box lid? | Spring collection or transmission system hatch/entry improvement needed*. (see photo #) The cover must overlap the framed opening and extend down around the frame at least two inches. [identify location of hatch in collection or transmission system] |
| sprRubbGaskLidN | (Source Data Springs) (Spring collection or distribution system hatches / manholes) Rubber gasket on the lid? | Spring collection or transmission system hatch/entry improvement needed*. (see photo #) Hatches / manholes in the spring collection and transmission system must be fitted with a solid, watertight cover with a rubber gasket. |
| sprSecureAccEntrN | (Source Data Springs) (Spring collection or distribution system hatches / manholes) Locked? | Spring collection or transmission system hatch/entry not locked. (see photo #) Hatch covers / manholes in the spring collection or transmission system must have a locking device. |
| sprSrcOfPolluNrSprY | (Source Data Springs) Are there any sources of pollution near the spring which could impact water quality? | Source of possible contamination in immediate area of spring. (see photo # ) In the vicinity of the spring there is [describe sources of pollution] that can potentially impact the water quality. [describe remedy] |
| sprSrcanimdropY | (Source Data Springs) Mice or other animals and their droppings in immediate area? | Mice or other animals and their droppings in immediate area of the spring (in spring house or collection box). (see photo # ) The mice or other animals and their droppings must be removed. Please refer to the Center for Disease Control (CDC) website regarding how to properly clean up this area to prevent contracting the Hantavirus pulmonary syndrome: http://www.cdc.gov/ncidod/diseases/hanta/hps/noframes/prevent3.htm. |
| sprSrcWTpGWN | Spring lacks Ground Water Rule sample tap.* | As required under the Ground Water Rule, a raw water sample tap must be installed so that water samples can be collected directly from the water source to determine the quality of the groundwater supply. The sample tap must be installed prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| sprTpPriPTN | Ground Water Rule sample tap must be relocated or reconfigured.* | As required under the Ground Water Rule, the raw water sample tap must represent water collected directly from the water source to determine the quality of the groundwater supply. The sample tap for the spring must be relocated so that it is prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| inflGllSourcePolluY | (Source Data Infiltration Galleries) Are there any sources of pollution near the infiltration gallery (e.g., agriculture/industrial activities, cleaning supplies, oil/fuel, etc.) which could impact water quality? | Source of possible contamination in immediate area of infiltration gallery. (see photo # ) In the vicinity of the infiltration gallery there is [describe sources of pollution] that can potentially impact the water quality. [describe remedy] |
| intStrmSrcePolluY | (Source Data Streams) Are there any sources of pollution near the stream (e.g., agriculture/industrial activities, cleaning supplies, oil/fuel, etc.) which could impact water quality? | Source of possible contamination in immediate area of stream. (see photo # ) In the vicinity of the stream there is [describe sources of pollution] that can potentially impact the water quality. [describe remedy] |
| intResvSrceSubPolluY | (Source Data Reservoirs) Are there any sources of pollution near the reservoirs, lakes and ponds and associated pumps (e.g., agriculture/industrial activities, cleaning supplies, oil/fuel, etc.) which could impact water quality? | Source of possible contamination in immediate area of reservoir. (see photo # ) In the vicinity of the reservoir there is [describe sources of pollution] that can potentially impact the water quality. [describe remedy] |
| EmergSrceSubPolluY | (Source Data Emergency Back-up Sources) Are there any sources of pollution near the emergency backup source (e.g., agriculture/industrial activities, cleaning supplies, oil/fuel, etc.) which could impact water quality? | Source of possible contamination in immediate area of emergency backup source. (see photo # ) In the vicinity of the emergency backup source there is [describe sources of pollution] that can potentially impact the water quality. [describe remedy] |
| RawTrans1ServConnY | (Raw Water Transmission) Are there any service connections to the raw water transmission line? | Customers connected to raw water transmission line*. Some customers are connected to the raw water transmission line to the treatment plant and are receiving untreated water. Delivery of non-potable water for human consumption is a public health risk. The service must be disconnected or appropriate treatment must be provided prior to use. [put site specific info about treating the water or disconnecting] |
| RawTrans2ServConnY | (Raw Water Transmission) Are there any service connections to the raw water transmission line? | Customers connected to raw water transmission line*. Some customers are connected to the raw water transmission line to the treatment plant and are receiving untreated water. Delivery of non-potable water for human consumption is a public health risk. The service must be disconnected or appropriate treatment must be provided prior to use. [put site specific info about treating the water or disconnecting] |
| distBstPSubjFldY1 | (Distribution Booster Pumps) Is the pump station subject to flooding? | Booster pump station subject to flooding [location of pump station]*. Flood water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. The pump must be re-located or adequately protected from flooding. |
| distBstPSubjFldY2 | (Distribution Booster Pumps) Is the pump station subject to flooding? | Booster pump station subject to flooding [location of pump station]*. Flood water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. The pump must be re-located or adequately protected from flooding. |
| distBstPSubjFldY3 | (Distribution Booster Pumps) Is the pump station subject to flooding? | Booster pump station subject to flooding [location of pump station]*. Flood water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. The pump must be re-located or adequately protected from flooding. |
| hydrTnkRustY | (Hydropneumatic Tanks) Is there evidence of severe rust? | Hydropneumatic tank has evidence of severe rust*. (see photo # ) Failure to maintain the structural and sanitary integrity of the tank could lead directly to contamination within the tank, illness and/or the loss of property. The rust on the tank must be repaired or the tank must be replaced. |
| hydrTnkLeakY | (Hydropneumatic Tanks) Is there evidence of water leaks? | Hydropneumatic tank has evidence of water leaks*. (see photo # ) Failure to maintain the structural and sanitary integrity of the tank could lead directly to contamination within the tank, illness and/or the loss of property. The leaks in the tank must be repaired or the tank must be replaced. |
| hydrTnkAirLeakY | (Hydropneumatic Tanks) Is there evidence of air leaks? | Hydropneumatic tank has evidence of air leaks*. (see photo # ) Failure to maintain the structural and sanitary integrity of the tank could lead directly to contamination within the tank, illness and/or the loss of property. The leaks in the tank must be repaired or the tank must be replaced. |
| hydrTnkFloodingY | (Hydropneumatic Tanks) Is there evidence of flooding (if in a vault)? | Hydropneumatic tank in a vault with evidence of flooding*. (see photo # ) Standing water creates an environment that could damage the structural and sanitary integrity of the tank. The hydropneumatic tank must be re-located or adequately protected from standing water. |
| hydrTnkComprAgeY | (Hydropneumatic Tanks) For any tank that uses an air compressor, is the tank age older than the life expectancy? | Pressure tank that uses an air compressor is older than the manufacturer’s life expectancy*. (see photo # ) In order to protect the structural integrity of the pressure tank (prevent tank explosion), tanks that exceed manufacturer’s life expectancy must be replaced. |
| gvTk1FloodingY | (Gravity Tanks) Is the site subject to flooding? | Storage tank located in an area subject to flooding. (see photo # ) [insert site specific problem and remedy] |
| gvTk1PropMaintN | (Gravity Tanks) Does the tank appear structurally sound? | Storage tank not structurally sound or properly maintained*. (see photo # ) The storage tank does not appear to be structurally sound. Specifically, the [tank component] of the tank must be evaluated by a professional engineer familiar with the construction of water-storage tanks to determine the integrity of the tank’s [tank component]. Failure to maintain the structural and sanitary integrity of the tank could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank must be made as soon as possible and it must be repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk1FounStrucSoundN | (Gravity Tanks) Does the foundation appear structurally sound? | Storage tank foundation does not appear to be structurally sound*. (see photo # ) The storage tank foundation does not appear to be structurally sound. It must be evaluated by a professional engineer familiar with the construction of water-storage tanks. Failure to maintain the structural and sanitary integrity of the tank foundation could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank foundation must be made as soon as possible and the foundation repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk1OpeningsY | (Gravity Tanks) Are there any unprotected openings in the tank (breaches, leaks, etc)? | Storage tank not sealed*. (see photo #) Other than the openings afforded by the #24-mesh screens on the vents and overflows, all openings must be sealed completely to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. [Describe specific openings such as: All openings between the roof and sidewalls must be sealed and watertight. Any openings from antennas, telemetry, and other appurtenances must be sealed and watertight.] |
| gvTk1InspectedN | (Gravity Tanks) If the tank is more than 10 years old, was it cleaned and inspected within the last 10 years? | Storage tank not cleaned and inspected within the last 10 years. The tank must be cleaned and inspected. Please see the enclosed Finished Water Storage Tank Inspection/Cleaning Checklist for a list of items that must be evaluated during the inspection. Tanks need to be periodically cleaned and inspected to prevent the growth of potentially harmful pathogens in the accumulated sediments and to address construction issues before they require major repairs. Inspections and cleaning may be done by a third-party professional or appropriately trained in-house staff. Please be aware that some tanks may be considered as confined spaces or hazardous environments; personnel working in or near the tanks should have all OSHA-required training, and proper safety equipment and procedures should be used at all times. After inspection and cleaning the tank must be disinfected according to AWWA standards (C652-92: Disinfection of Water Storage Facilities). In order to correct this significant deficiency, you must provide EPA with the following documentation: A completed copy of the Finished Water Storage Tank Inspection/Cleaning Checklist. A copy of inspection results and labeled photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk1OvFlSepN | (Gravity Tanks) Does the tank have an overflow separate from the vent? @ | No overflow on finished water storage tank*. In order to protect the integrity of the tank in the case of control system failure leading to overfilling, the tank must have an overflow that is separate from the vent. |
| gvTk1OvFlAccessN | (Gravity Tanks) Is the overflow accessible for inspection? | Unknown integrity of storage tank overflow [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank overflow [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk1OvFl24MeshN | (Gravity Tanks) Overflow has a #24-mesh screen OR a duckbill valve OR a properly sealed flapper valve with screen inside (the EPA recommends a #24-mesh screen)? | Overflow screening on finished water storage tank improvement needed*. (see photo #) Overflows must be fitted with non-corrodible #24-mesh screen, or a properly sealed flapper or duckbill valve to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the pipe at a location least susceptible to vandalism. When a flapper valve is used, a screen must be placed inside the valve (the EPA Region 8 recommends non-corrodible #24-mesh screen be used). In cold climates, use of a flapper or duckbill valve should be considered to minimize air movement and hence ice formation in the tank. In cold climates, provisions should be considered to prevent the flapper or duckbill from freezing shut. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk1OvFlTerm12InN | (Gravity Tanks) Does the overflow line terminate no less than 12 inches but no more than 24 inches above the ground surface? | Overflow on finished water storage tank discharges at improper height*. (see photo #) Overflow must be piped to an elevation between 12 and 24 inches above the ground surface and discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk1OvDrainStructN | (Gravity Tanks) Does the overflow discharge over an inlet structure, splash plate, or engineered rip-rap? | Overflow discharge point on finished water storage tank improvement needed*. (see photo #) Overflow must discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk1OvFlConnSewerN | (Gravity Tanks) Does the overflow have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Overflow on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain*. (see photo #) No overflow may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the overflow pipe terminates at least three pipe diameters above the ground level at the sewer or storm drain, or over a splash pad. |
| gvTk1DLAccessblN | (Gravity Tanks) Is the drain accessible for inspection? | Unknown integrity of storage tank drain [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank drain [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk1DLAirGapN | (Gravity Tanks) Does the drain pipe have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Drain on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain*. (see photo #) No drain may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the drain pipe terminates at least three pipe diameters above the ground level at the sewer drain, storm drain, splash pad or engineered rip-rap. |
| gvTk1VentSepN | (Gravity Tanks) Does the tank have a vent separate from the overflow? | No vent on finished water storage tank*. In order to protect the structural integrity of the tank during changes to tank water levels, and other events affecting the confined air space, the tank must have a vent that is separate from the overflow. |
| gvTk1AirVentAccessN | (Gravity Tanks) Is the vent accessible for inspection? | Unknown integrity of storage tank air vent [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank air vent [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk1AirVntMeshN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Is there #24-mesh screen? | Air vent screening on finished water storage tank needs improvement*. (see photo #) The vent must be fitted with non-corrodible #24-mesh screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. Prior to installing the screen, the PWS should evaluate whether the tank needs a vacuum/pressure relief valve or another mechanism to prevent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk1AirVnt24AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Downturned vent: Is the vent at least 24“ above the roof? | Downturned air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24” above the tank surface to prevent inhalation of contaminants by the tank. |
| gvTk1AirVentSoldCovN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is there a solid cover down to the bottom of the vent screen? | Air vent on finished water storage tank does not have a solid cover*. (see photo #) For non-downturned vents, the screen must have a solid cover down to the bottom of the vent screen to prevent rain and snow, and minimize dust and sunlight, from entering the tank. If the cover is installed in a manner that restricts the size of the vent opening it may result in insufficient airflow and subsequent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require evaluation by a licensed engineer to ensure that no damage will occur to the existing water tank as a result of the modifications. For elevated tanks and standpipes, the EPA strongly recommends that the system install a vent with an automatic re-setting vacuum/pressure relief mechanism if one is not already in place. |
| gvTk1AirVnt8AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is the screen at least 8” above the roof surface? | Air vent on finished water storage tank is not elevated above the roof at the required height*. (see photo #) For non-downturned vents, the bottom of the vent screen must be at least 8” above the tank roof to prevent inhalation of contaminants by the tank. |
| gvTk1AirVen24MeshN | (Gravity Tanks) Below Ground (buried or partially buried) Is air vent covered with #24-mesh screen? | Air vent screening on finished water storage tank improvement needed*. (see photo #) The vent must be fitted with non-corrodible #24-mesh screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk1AirVnTermDwnN | (Gravity Tanks) Below Ground (buried or partially buried) Does the air vent terminate downward? | Air vent on finished water storage tank does not terminate in a downturned position*. (see photo #) On buried or partially buried tanks the air vent must terminate in a downturned position. |
| gvTk1AirVnTrmAbvRfN | (Gravity Tanks) Below Ground (buried or partially buried) Is the air vent at least 24” above the roof or ground surface (whichever is higher)? | Air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24 inches above the roof or ground surface (whichever is higher) to prevent rain from entering and to prevent inhalation of contaminants by the tank. |
| gvTk1AHAccessableN | (Gravity Tanks) Is the hatch accessible for inspection? | Unknown integrity of storage tank access hatch [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank access hatch [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk1bgAH24AboveRfN | (Gravity Tanks) For below ground tanks where the roof is completely buried, is the hatch raised at least 24” above ground level? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the ground surface. |
| gvTk1pbAH24AboveRfN | (Gravity Tanks) For partially buried tanks where the roof is visible, is the hatch raised at least 24” above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the surface of the roof. |
| gvTk1agAH4AboveRfN | (Gravity Tanks) For above ground tanks (ground level or elevated/standpipe): Is the hatch raised 4“ above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be framed at least four inches above the surface of the roof. |
| gvTk1AHShoeBxLidN | (Gravity Tanks) Does the hatch have a shoe box lid? | Hatch on Finished Water Storage Tank does not have a shoe box lid*. (see photo #) The tank hatch must be fitted with a solid watertight cover which extends down around the frame at least two inches. |
| gvTk1AHRubberGaskN | (Gravity Tanks) Is the lid tight and sealed with a rubber gasket? | Hatch on Finished Water Storage Tank does not have a gasket that creates a watertight seal. (see photo #) The tank hatch must have a rubber gasket to seal the hatch lid to the frame tightly to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| gvTk1AHALockedN | (Gravity Tanks) Is the hatch locked? | Hatch on Finished Water Storage Tank does not have a locking device. (see photo #) The cover must have a locking device. |
| gvTk2FloodingY | (Gravity Tanks) Is the site subject to flooding? | Storage tank located in an area subject to flooding. (see photo # ) [insert site specific problem and remedy] |
| gvTk2PropMaintN | (Gravity Tanks) Does the tank appear structurally sound? | Storage tank not structurally sound or properly maintained*. (see photo # ) The storage tank does not appear to be structurally sound. Specifically, the [tank component] of the tank must be evaluated by a professional engineer familiar with the construction of water-storage tanks to determine the integrity of the tank’s [tank component]. Failure to maintain the structural and sanitary integrity of the tank could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank must be made as soon as possible and it must be repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk2FounStrucSoundN | (Gravity Tanks) Does the foundation appear structurally sound? | Storage tank foundation does not appear to be structurally sound*. (see photo # ) The storage tank foundation does not appear to be structurally sound. It must be evaluated by a professional engineer familiar with the construction of water-storage tanks. Failure to maintain the structural and sanitary integrity of the tank foundation could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank foundation must be made as soon as possible and the foundation repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk2OpeningsY | (Gravity Tanks) Are there any unprotected openings in the tank (breaches, leaks, etc)? | Storage tank not sealed*. (see photo #) Other than the openings afforded by the #24-mesh screens on the vents and overflows, all openings must be sealed completely to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. [Describe specific openings such as: All openings between the roof and sidewalls must be sealed and watertight. Any openings from antennas, telemetry, and other appurtenances must be sealed and watertight.] |
| gvTk2InspectedN | (Gravity Tanks) If the tank is more than 10 years old, was it cleaned and inspected within the last 10 years? | Storage tank not cleaned and inspected within the last 10 years. The tank must be cleaned and inspected. Please see the enclosed Finished Water Storage Tank Inspection/Cleaning Checklist for a list of items that must be evaluated during the inspection. Tanks need to be periodically cleaned and inspected to prevent the growth of potentially harmful pathogens in the accumulated sediments and to address construction issues before they require major repairs. Inspections and cleaning may be done by a third-party professional or appropriately trained in-house staff. Please be aware that some tanks may be considered as confined spaces or hazardous environments; personnel working in or near the tanks should have all OSHA-required training, and proper safety equipment and procedures should be used at all times. After inspection and cleaning the tank must be disinfected according to AWWA standards (C652-92: Disinfection of Water Storage Facilities). In order to correct this significant deficiency, you must provide EPA with the following documentation: A completed copy of the Finished Water Storage Tank Inspection/Cleaning Checklist. A copy of inspection results and labeled photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk2OvFlSepN | (Gravity Tanks) Does the tank have an overflow separate from the vent? @ | No overflow on finished water storage tank*. In order to protect the integrity of the tank in the case of control system failure leading to overfilling, the tank must have an overflow that is separate from the vent. |
| gvTk2OvFlAccessN | (Gravity Tanks) Is the overflow accessible for inspection? | Unknown integrity of storage tank overflow [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank overflow [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk2OvFl24MeshN | (Gravity Tanks) Overflow has a #24-mesh screen OR a duckbill valve OR a properly sealed flapper valve with screen inside (the EPA recommends a #24-mesh screen)? | Overflow screening on finished water storage tank improvement needed*. (see photo #) Overflows must be fitted with non-corrodible #24-mesh screen, or a properly sealed flapper or duckbill valve to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the pipe at a location least susceptible to vandalism. When a flapper valve is used, a screen must be placed inside the valve (EPA Region 8 recommends non-corrodible #24-mesh screen be used). In cold climates, use of a flapper or duckbill valve should be considered to minimize air movement and hence ice formation in the tank. In cold climates, provisions should be considered to prevent the flapper or duckbill from freezing shut. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk2OvFlTerm12InN | (Gravity Tanks) Does the overflow line terminate no less than 12 inches but no more than 24 inches above the ground surface? | Overflow on finished water storage tank discharges at improper height*. (see photo #) Overflow must be piped to an elevation between 12 and 24 inches above the ground surface and discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk2OvDrainStructN | (Gravity Tanks) Does the overflow discharge over an inlet structure, splash plate, or engineered rip-rap? | Overflow discharge point on finished water storage tank improvement needed*. (see photo #) Overflow must discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk2OvFlConnSewerN | (Gravity Tanks) Does the overflow have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Overflow on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain. (see photo #) No overflow may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the overflow pipe terminates at least three pipe diameters above the ground level at the sewer or storm drain, or over a splash pad. |
| gvTk2DLAccessblN | (Gravity Tanks) Is the drain accessible for inspection? | Unknown integrity of storage tank drain [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank drain [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk2DLAirGapN | (Gravity Tanks) Does the drain pipe have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Drain on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain*. (see photo #) No drain may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the drain pipe terminates at least three pipe diameters above the ground level at the sewer drain, storm drain, splash pad or engineered rip-rap. |
| gvTk2VentSepN | (Gravity Tanks) Does the tank have a vent separate from the overflow? | No vent on finished water storage tank*. In order to protect the structural integrity of the tank during changes to tank water levels, and other events affecting the confined air space, the tank must have a vent that is separate from the overflow. |
| gvTk2AirVentAccessN | (Gravity Tanks) Is the vent accessible for inspection? | Unknown integrity of storage tank air vent [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank air vent [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. The EPA will review the inspection report and may require additional corrective actions. |
| gvTk2AirVntMeshN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Is there #24-mesh screen? | Air vent screening on finished water storage tank needs improvement*. (see photo #) The vent must be fitted with non-corrodible #24-mesh screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. Prior to installing the screen, the PWS should evaluate whether the tank needs a vacuum/pressure relief valve or another mechanism to prevent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk2AirVnt24AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Downturned vent: Is the vent at least 24“ above the roof? | Downturned air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24” above the tank surface to prevent inhalation of contaminants by the tank. |
| gvTk2AirVentSoldCovN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is there a solid cover down to the bottom of the vent screen? | Air vent on finished water storage tank does not have a solid cover*. (see photo #) For non-downturned vents, the screen must have a solid cover down to the bottom of the vent screen to prevent rain and snow, and minimize dust and sunlight, from entering the tank. If the cover is installed in a manner that restricts the size of the vent opening it may result in insufficient airflow and subsequent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require evaluation by a licensed engineer to ensure that no damage will occur to the existing water tank as a result of the modifications. For elevated tanks and standpipes, the EPA strongly recommends that the system install a vent with an automatic re-setting vacuum/pressure relief mechanism if one is not already in place. |
| gvTk2AirVnt8AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is the screen at least 8” above the roof surface? | Air vent on finished water storage tank is not elevated above the roof at the required height*. (see photo #) For non-downturned vents, the bottom of the vent screen must be at least 8” above the tank roof to prevent inhalation of contaminants by the tank. |
| gvTk2AirVen24MeshN | (Gravity Tanks) Below Ground (buried or partially buried) Is air vent covered with #24-mesh screen? | Air vent screening on finished water storage tank improvement needed*. (see photo #) The vent must be fitted with non-corrodible #24-mesh screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk2AirVnTermDwnN | (Gravity Tanks) Below Ground (buried or partially buried) Does the air vent terminate downward? | Air vent on finished water storage tank does not terminate in a downturned position*. (see photo #) On buried or partially buried tanks the air vent must terminate in a downturned position. |
| gvTk2AirVnTrmAbvRfN | (Gravity Tanks) Below Ground (buried or partially buried) Is the air vent at least 24” above the roof or ground surface (whichever is higher)? | Air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24 inches above the roof or ground surface (whichever is higher) to prevent rain from entering and to prevent inhalation of contaminants by the tank. |
| gvTk2AHAccessableN | (Gravity Tanks) Is the hatch accessible for inspection? | Unknown integrity of storage tank access hatch [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank access hatch [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. The EPA will review the inspection report and may require additional corrective actions. |
| gvTk2bgAH24AboveRfN | (Gravity Tanks) For below ground tanks where the roof is completely buried, is the hatch raised at least 24” above ground level? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the ground surface. |
| gvTk2pbAH24AboveRfN | (Gravity Tanks) For partially buried tanks where the roof is visible, is the hatch raised at least 24” above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the surface of the roof. |
| gvTk2agAH4AboveRfN | (Gravity Tanks) For above ground tanks (ground level or elevated/standpipe): Is the hatch raised 4“ above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be framed at least four inches above the surface of the roof. |
| gvTk2AHShoeBxLidN | (Gravity Tanks) Does the hatch have a shoe box lid? | Hatch on Finished Water Storage Tank does not have a shoe box lid*. (see photo #) The tank hatch must be fitted with a solid watertight cover which extends down around the frame at least two inches. |
| gvTk2AHRubberGaskN | (Gravity Tanks) Is the lid tight and sealed with a rubber gasket? | Hatch on Finished Water Storage Tank does not have a gasket that creates a watertight seal. (see photo #) The tank hatch must have a rubber gasket to seal the hatch lid to the frame tightly to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| gvTk2AHALockedN | (Gravity Tanks) Is the hatch locked? | Hatch on Finished Water Storage Tank does not have a locking device. (see photo #) The cover must have a locking device. |
| gvTk3FloodingY | (Gravity Tanks) Is the site subject to flooding? | Storage tank located in an area subject to flooding. (see photo # ) [insert site specific problem and remedy] |
| gvTk3PropMaintN | (Gravity Tanks) Does the tank appear structurally sound? | Storage tank not structurally sound or properly maintained*. (see photo # ) The storage tank does not appear to be structurally sound. Specifically, the [tank component] of the tank must be evaluated by a professional engineer familiar with the construction of water-storage tanks to determine the integrity of the tank’s [tank component]. Failure to maintain the structural and sanitary integrity of the tank could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank must be made as soon as possible and it must be repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk3FounStrucSoundN | (Gravity Tanks) Does the foundation appear structurally sound? | Storage tank foundation does not appear to be structurally sound*. (see photo # ) The storage tank foundation does not appear to be structurally sound. It must be evaluated by a professional engineer familiar with the construction of water-storage tanks. Failure to maintain the structural and sanitary integrity of the tank foundation could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank foundation must be made as soon as possible and the foundation repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk3OpeningsY | (Gravity Tanks) Are there any unprotected openings in the tank (breaches, leaks, etc)? | Storage tank not sealed*. (see photo #) Other than the openings afforded by the #24-mesh screens on the vents and overflows, all openings must be sealed completely to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. [Describe specific openings such as: All openings between the roof and sidewalls must be sealed and watertight. Any openings from antennas, telemetry, and other appurtenances must be sealed and watertight.] |
| gvTk3InspectedN | (Gravity Tanks) If the tank is more than 10 years old, was it cleaned and inspected within the last 10 years? | Storage tank not cleaned and inspected within the last 10 years. The tank must be cleaned and inspected. Please see the enclosed Finished Water Storage Tank Inspection/Cleaning Checklist for a list of items that must be evaluated during the inspection. Tanks need to be periodically cleaned and inspected to prevent the growth of potentially harmful pathogens in the accumulated sediments and to address construction issues before they require major repairs. Inspections and cleaning may be done by a third-party professional or appropriately trained in-house staff. Please be aware that some tanks may be considered as confined spaces or hazardous environments; personnel working in or near the tanks should have all OSHA-required training, and proper safety equipment and procedures should be used at all times. After inspection and cleaning the tank must be disinfected according to AWWA standards (C652-92: Disinfection of Water Storage Facilities). In order to correct this significant deficiency, you must provide EPA with the following documentation: A completed copy of the Finished Water Storage Tank Inspection/Cleaning Checklist. A copy of inspection results and labeled photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk3OvFlSepN | (Gravity Tanks) Does the tank have an overflow separate from the vent? @ | No overflow on finished water storage tank*. In order to protect the integrity of the tank in the case of control system failure leading to overfilling, the tank must have an overflow that is separate from the vent. |
| gvTk3OvFlAccessN | (Gravity Tanks) Is the overflow accessible for inspection? | Unknown integrity of storage tank overflow [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank overflow [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. The EPA will review the inspection report and may require additional corrective actions. |
| gvTk3OvFl24MeshN | (Gravity Tanks) Overflow has a #24-mesh screen OR a duckbill valve OR a properly sealed flapper valve with screen inside (The EPA recommends a #24-mesh screen)? | Overflow screening on finished water storage tank improvement needed*. (see photo #) Overflows must be fitted with non-corrodible #24-mesh screen, or a properly sealed flapper or duckbill valve to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the pipe at a location least susceptible to vandalism. When a flapper valve is used, a screen must be placed inside the valve (EPA Region 8 recommends non-corrodible #24-mesh screen be used). In cold climates, use of a flapper or duckbill valve should be considered to minimize air movement and hence ice formation in the tank. In cold climates, provisions should be considered to prevent the flapper or duckbill from freezing shut. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk3OvFlTerm12InN | (Gravity Tanks) Does the overflow line terminate no less than 12 inches but no more than 24 inches above the ground surface? | Overflow on finished water storage tank discharges at improper height*. (see photo #) Overflow must be piped to an elevation between 12 and 24 inches above the ground surface and discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk3OvDrainStructN | (Gravity Tanks) Does the overflow discharge over an inlet structure, splash plate, or engineered rip-rap? | Overflow discharge point on finished water storage tank improvement needed*. (see photo #) Overflow must discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk3OvFlConnSewerN | (Gravity Tanks) Does the overflow have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Overflow on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain. (see photo #) No overflow may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the overflow pipe terminates at least three pipe diameters above the ground level at the sewer or storm drain, or over a splash pad. |
| gvTk3DLAccessblN | (Gravity Tanks) Is the drain accessible for inspection? | Unknown integrity of storage tank drain [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank drain [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk3DLAirGapN | (Gravity Tanks) Does the drain pipe have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Drain on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain*. (see photo #) No drain may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the drain pipe terminates at least three pipe diameters above the ground level at the sewer drain, storm drain, splash pad or engineered rip-rap. |
| gvTk3VentSepN | (Gravity Tanks) Does the tank have a vent separate from the overflow? | No vent on finished water storage tank*. In order to protect the structural integrity of the tank during changes to tank water levels, and other events affecting the confined air space, the tank must have a vent that is separate from the overflow. |
| gvTk3AirVentAccessN | (Gravity Tanks) Is the vent accessible for inspection? | Unknown integrity of storage tank air vent [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank air vent [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. The EPA will review the inspection report and may require additional corrective actions. |
| gvTk3AirVntMeshN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Is there #24-mesh screen? | Air vent screening on finished water storage tank needs improvement*. (see photo #) The vent must be fitted with non-corrodible #24-mesh screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. Prior to installing the screen, the PWS should evaluate whether the tank needs a vacuum/pressure relief valve or another mechanism to prevent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk3AirVnt24AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Downturned vent: Is the vent at least 24“ above the roof? | Downturned air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24” above the tank surface to prevent inhalation of contaminants by the tank. |
| gvTk3AirVentSoldCovN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is there a solid cover down to the bottom of the vent screen? | Air vent on finished water storage tank does not have a solid cover*. (see photo #) For non-downturned vents, the screen must have a solid cover down to the bottom of the vent screen to prevent rain and snow, and minimize dust and sunlight, from entering the tank. If the cover is installed in a manner that restricts the size of the vent opening it may result in insufficient airflow and subsequent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require evaluation by a licensed engineer to ensure that no damage will occur to the existing water tank as a result of the modifications. For elevated tanks and standpipes, the EPA strongly recommends that the system install a vent with an automatic re-setting vacuum/pressure relief mechanism if one is not already in place. |
| gvTk3AirVnt8AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is the screen at least 8” above the roof surface? | Air vent on finished water storage tank is not elevated above the roof at the required height*. (see photo #) For non-downturned vents, the bottom of the vent screen must be at least 8” above the tank roof to prevent inhalation of contaminants by the tank. |
| gvTk3AirVen24MeshN | (Gravity Tanks) Below Ground (buried or partially buried) Is air vent covered with #24-mesh screen? | Air vent screening on finished water storage tank improvement needed*. (see photo #) The vent must be fitted with non-corrodible #24-mesh screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk3AirVnTermDwnN | (Gravity Tanks) Below Ground (buried or partially buried) Does the air vent terminate downward? | Air vent on finished water storage tank does not terminate in a downturned position*. (see photo #) On buried or partially buried tanks the air vent must terminate in a downturned position. |
| gvTk3AirVnTrmAbvRfN | (Gravity Tanks) Below Ground (buried or partially buried) Is the air vent at least 24” above the roof or ground surface (whichever is higher)? | Air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24 inches above the roof or ground surface (whichever is higher) to prevent rain from entering and to prevent inhalation of contaminants by the tank. |
| gvTk3AHAccessableN | (Gravity Tanks) Is the hatch accessible for inspection? | Unknown integrity of storage tank access hatch [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank access hatch [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. The EPA will review the inspection report and may require additional corrective actions. |
| gvTk3bgAH24AboveRfN | (Gravity Tanks) For below ground tanks where the roof is completely buried, is the hatch raised at least 24” above ground level? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the ground surface. |
| gvTk3pbAH24AboveRfN | (Gravity Tanks) For partially buried tanks where the roof is visible, is the hatch raised at least 24” above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the surface of the roof. |
| gvTk3agAH4AboveRfN | (Gravity Tanks) For above ground tanks (ground level or elevated/standpipe): Is the hatch raised 4“ above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be framed at least four inches above the surface of the roof. |
| gvTk3AHShoeBxLidN | (Gravity Tanks) Does the hatch have a shoe box lid? | Hatch on Finished Water Storage Tank does not have a shoe box lid*. (see photo #) The tank hatch must be fitted with a solid watertight cover which extends down around the frame at least two inches. |
| gvTk3AHRubberGaskN | (Gravity Tanks) Is the lid tight and sealed with a rubber gasket? | Hatch on Finished Water Storage Tank does not have a gasket that creates a watertight seal. (see photo #) The tank hatch must have a rubber gasket to seal the hatch lid to the frame tightly to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| gvTk3AHALockedN | (Gravity Tanks) Is the hatch locked? | Hatch on Finished Water Storage Tank does not have a locking device. (see photo #) The cover must have a locking device. |
| gvTk4FloodingY | (Gravity Tanks) Is the site subject to flooding? | Storage tank located in an area subject to flooding. (see photo # ) [insert site specific problem and remedy] |
| gvTk4PropMaintN | (Gravity Tanks) Does the tank appear structurally sound? | Storage tank not structurally sound or properly maintained*. (see photo # ) The storage tank does not appear to be structurally sound. Specifically, the [tank component] of the tank must be evaluated by a professional engineer familiar with the construction of water-storage tanks to determine the integrity of the tank’s [tank component]. Failure to maintain the structural and sanitary integrity of the tank could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank must be made as soon as possible and it must be repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk4FounStrucSoundN | (Gravity Tanks) Does the foundation appear structurally sound? | Storage tank foundation does not appear to be structurally sound*. (see photo # ) The storage tank foundation does not appear to be structurally sound. It must be evaluated by a professional engineer familiar with the construction of water-storage tanks. Failure to maintain the structural and sanitary integrity of the tank foundation could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank foundation must be made as soon as possible and the foundation repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk4OpeningsY | (Gravity Tanks) Are there any unprotected openings in the tank (breaches, leaks, etc)? | Storage tank not sealed*. (see photo #) Other than the openings afforded by the #24-mesh screens on the vents and overflows, all openings must be sealed completely to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. [Describe specific openings such as: All openings between the roof and sidewalls must be sealed and watertight. Any openings from antennas, telemetry, and other appurtenances must be sealed and watertight.] |
| gvTk4InspectedN | (Gravity Tanks) If the tank is more than 10 years old, was it cleaned and inspected within the last 10 years? | Storage tank not cleaned and inspected within the last 10 years. The tank must be cleaned and inspected. Please see the enclosed Finished Water Storage Tank Inspection/Cleaning Checklist for a list of items that must be evaluated during the inspection. Tanks need to be periodically cleaned and inspected to prevent the growth of potentially harmful pathogens in the accumulated sediments and to address construction issues before they require major repairs. Inspections and cleaning may be done by a third-party professional or appropriately trained in-house staff. Please be aware that some tanks may be considered as confined spaces or hazardous environments; personnel working in or near the tanks should have all OSHA-required training, and proper safety equipment and procedures should be used at all times. After inspection and cleaning the tank must be disinfected according to AWWA standards (C652-92: Disinfection of Water Storage Facilities). In order to correct this significant deficiency, you must provide EPA with the following documentation: A completed copy of the Finished Water Storage Tank Inspection/Cleaning Checklist. A copy of inspection results and labeled photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk4OvFlSepN | (Gravity Tanks) Does the tank have an overflow separate from the vent? @ | No overflow on finished water storage tank*. In order to protect the integrity of the tank in the case of control system failure leading to overfilling, the tank must have an overflow that is separate from the vent. |
| gvTk4OvFlAccessN | (Gravity Tanks) Is the overflow accessible for inspection? | Unknown integrity of storage tank overflow [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank overflow [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk4OvFl24MeshN | (Gravity Tanks) Overflow has a #24-mesh screen OR a duckbill valve OR a properly sealed flapper valve with screen inside (The EPA recommends a #24-mesh screen)? | Overflow screening on finished water storage tank improvement needed*. (see photo #) Overflows must be fitted with non-corrodible #24-mesh screen, or a properly sealed flapper or duckbill valve to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the pipe at a location least susceptible to vandalism. When a flapper valve is used, a screen must be placed inside the valve (EPA Region 8 recommends non-corrodible #24-mesh screen be used). In cold climates, use of a flapper or duckbill valve should be considered to minimize air movement and hence ice formation in the tank. In cold climates, provisions should be considered to prevent the flapper or duckbill from freezing shut. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk4OvFlTerm12InN | (Gravity Tanks) Does the overflow line terminate no less than 12 inches but no more than 24 inches above the ground surface? | Overflow on finished water storage tank discharges at improper height*. (see photo #) Overflow must be piped to an elevation between 12 and 24 inches above the ground surface and discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk4OvDrainStructN | (Gravity Tanks) Does the overflow discharge over an inlet structure, splash plate, or engineered rip-rap? | Overflow discharge point on finished water storage tank improvement needed*. (see photo #) Overflow must discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk4OvFlConnSewerN | (Gravity Tanks) Does the overflow have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Overflow on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain. (see photo #) No overflow may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the overflow pipe terminates at least three pipe diameters above the ground level at the sewer or storm drain, or over a splash pad. |
| gvTk4DLAccessblN | (Gravity Tanks) Is the drain accessible for inspection? | Unknown integrity of storage tank drain [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank drain [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk4DLAirGapN | (Gravity Tanks) Does the drain pipe have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Drain on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain*. (see photo #) No drain may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the drain pipe terminates at least three pipe diameters above the ground level at the sewer drain, storm drain, splash pad or engineered rip-rap. |
| gvTk4VentSepN | (Gravity Tanks) Does the tank have a vent separate from the overflow? | No vent on finished water storage tank*. In order to protect the structural integrity of the tank during changes to tank water levels, and other events affecting the confined air space, the tank must have a vent that is separate from the overflow. |
| gvTk4AirVentAccessN | (Gravity Tanks) Is the vent accessible for inspection? | Unknown integrity of storage tank air vent [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank air vent [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. The EPA will review the inspection report and may require additional corrective actions. |
| gvTk4AirVntMeshN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Is there #24-mesh screen? | Air vent screening on finished water storage tank needs improvement*. (see photo #) The vent must be fitted with non-corrodible #24-mesh screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. Prior to installing the screen, the PWS should evaluate whether the tank needs a vacuum/pressure relief valve or another mechanism to prevent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk4AirVnt24AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Downturned vent: Is the vent at least 24“ above the roof? | Downturned air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24” above the tank surface to prevent inhalation of contaminants by the tank. |
| gvTk4AirVentSoldCovN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is there a solid cover down to the bottom of the vent screen? | Air vent on finished water storage tank does not have a solid cover*. (see photo #) For non-downturned vents, the screen must have a solid cover down to the bottom of the vent screen to prevent rain and snow, and minimize dust and sunlight, from entering the tank. If the cover is installed in a manner that restricts the size of the vent opening it may result in insufficient airflow and subsequent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require evaluation by a licensed engineer to ensure that no damage will occur to the existing water tank as a result of the modifications. For elevated tanks and standpipes, the EPA strongly recommends that the system install a vent with an automatic re-setting vacuum/pressure relief mechanism if one is not already in place. |
| gvTk4AirVnt8AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is the screen at least 8” above the roof surface? | Air vent on finished water storage tank is not elevated above the roof at the required height*. (see photo #) For non-downturned vents, the bottom of the vent screen must be at least 8” above the tank roof to prevent inhalation of contaminants by the tank. |
| gvTk4AirVen24MeshN | (Gravity Tanks) Below Ground (buried or partially buried) Is air vent covered with #24-mesh screen? | Air vent screening on finished water storage tank improvement needed*. (see photo #) The vent must be fitted with a #24-mesh non corrodible screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. |
| gvTk4AirVnTermDwnN | (Gravity Tanks) Below Ground (buried or partially buried) Does the air vent terminate downward? | Air vent on finished water storage tank does not terminate in a downturned position*. (see photo #) On buried or partially buried tanks the air vent must terminate in a downturned position. |
| gvTk4AirVnTrmAbvRfN | (Gravity Tanks) Below Ground (buried or partially buried) Is the air vent at least 24” above the roof or ground surface (whichever is higher)? | Air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24 inches above the roof or ground surface (whichever is higher) to prevent rain from entering and to prevent inhalation of contaminants by the tank. |
| gvTk4AHAccessableN | (Gravity Tanks) Is the hatch accessible for inspection? | Unknown integrity of storage tank access hatch [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank access hatch [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. The EPA will review the inspection report and may require additional corrective actions. |
| gvTk4bgAH24AboveRfN | (Gravity Tanks) For below ground tanks where the roof is completely buried, is the hatch raised at least 24” above ground level? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the ground surface. |
| gvTk4pbAH24AboveRfN | (Gravity Tanks) For partially buried tanks where the roof is visible, is the hatch raised at least 24” above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the surface of the roof. |
| gvTk4agAH4AboveRfN | (Gravity Tanks) For above ground tanks (ground level or elevated/standpipe): Is the hatch raised 4“ above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be framed at least four inches above the surface of the roof. |
| gvTk4AHShoeBxLidN | (Gravity Tanks) Does the hatch have a shoe box lid? | Hatch on Finished Water Storage Tank does not have a shoe box lid*. (see photo #) The tank hatch must be fitted with a solid watertight cover which extends down around the frame at least two inches. |
| gvTk4AHRubberGaskN | (Gravity Tanks) Is the lid tight and sealed with a rubber gasket? | Hatch on Finished Water Storage Tank does not have a gasket that creates a watertight seal. (see photo #) The tank hatch must have a rubber gasket to seal the hatch lid to the frame tightly to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| gvTk4AHALockedN | (Gravity Tanks) Is the hatch locked? | Hatch on Finished Water Storage Tank does not have a locking device. (see photo #) The cover must have a locking device. |
| gvTk5FloodingY | (Gravity Tanks) Is the site subject to flooding? | Storage tank located in an area subject to flooding. (see photo # ) [insert site specific problem and remedy] |
| gvTk5PropMaintN | (Gravity Tanks) Does the tank appear structurally sound? | Storage tank not structurally sound or properly maintained*. (see photo # ) The storage tank does not appear to be structurally sound. Specifically, the [tank component] of the tank must be evaluated by a professional engineer familiar with the construction of water-storage tanks to determine the integrity of the tank’s [tank component]. Failure to maintain the structural and sanitary integrity of the tank could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank must be made as soon as possible and it must be repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk5FounStrucSoundN | (Gravity Tanks) Does the foundation appear structurally sound? | Storage tank foundation does not appear to be structurally sound*. (see photo # ) The storage tank foundation does not appear to be structurally sound. It must be evaluated by a professional engineer familiar with the construction of water-storage tanks. Failure to maintain the structural and sanitary integrity of the tank foundation could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank foundation must be made as soon as possible and the foundation repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk5OpeningsY | (Gravity Tanks) Are there any unprotected openings in the tank (breaches, leaks, etc)? | Storage tank not sealed*. (see photo #) Other than the openings afforded by the #24-mesh screens on the vents and overflows, all openings must be sealed completely to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. [Describe specific openings such as: All openings between the roof and sidewalls must be sealed and watertight. Any openings from antennas, telemetry, and other appurtenances must be sealed and watertight.] |
| gvTk5InspectedN | (Gravity Tanks) If the tank is more than 10 years old, was it cleaned and inspected within the last 10 years? | Storage tank not cleaned and inspected within the last 10 years. The tank must be cleaned and inspected. Please see the enclosed Finished Water Storage Tank Inspection/Cleaning Checklist for a list of items that must be evaluated during the inspection. Tanks need to be periodically cleaned and inspected to prevent the growth of potentially harmful pathogens in the accumulated sediments and to address construction issues before they require major repairs. Inspections and cleaning may be done by a third-party professional or appropriately trained in-house staff. Please be aware that some tanks may be considered as confined spaces or hazardous environments; personnel working in or near the tanks should have all OSHA-required training, and proper safety equipment and procedures should be used at all times. After inspection and cleaning the tank must be disinfected according to AWWA standards (C652-92: Disinfection of Water Storage Facilities). In order to correct this significant deficiency, you must provide EPA with the following documentation: A completed copy of the Finished Water Storage Tank Inspection/Cleaning Checklist. A copy of inspection results and labeled photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk5OvFlSepN | (Gravity Tanks) Does the tank have an overflow separate from the vent? @ | No overflow on finished water storage tank*. In order to protect the integrity of the tank in the case of control system failure leading to overfilling, the tank must have an overflow that is separate from the vent. |
| gvTk5OvFlAccessN | (Gravity Tanks) Is the overflow accessible for inspection? | Unknown integrity of storage tank overflow [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank overflow [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk5OvFl24MeshN | (Gravity Tanks) Overflow has a #24-mesh screen OR a duckbill valve OR a properly sealed flapper valve with screen inside (The EPA recommends a #24-mesh screen)? | Overflow screening on finished water storage tank improvement needed*. (see photo #) Overflows must be fitted with non-corrodible #24-mesh screen, or a properly sealed flapper or duckbill valve to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the pipe at a location least susceptible to vandalism. When a flapper valve is used, a screen must be placed inside the valve (EPA Region 8 recommends non-corrodible #24-mesh screen be used). In cold climates, use of a flapper or duckbill valve should be considered to minimize air movement and hence ice formation in the tank. In cold climates, provisions should be considered to prevent the flapper or duckbill from freezing shut. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk5OvFlTerm12InN | (Gravity Tanks) Does the overflow line terminate no less than 12 inches but no more than 24 inches above the ground surface? | Overflow on finished water storage tank discharges at improper height*. (see photo #) Overflow must be piped to an elevation between 12 and 24 inches above the ground surface and discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk5OvDrainStructN | (Gravity Tanks) Does the overflow discharge over an inlet structure, splash plate, or engineered rip-rap? | Overflow discharge point on finished water storage tank improvement needed*. (see photo #) Overflow must discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk5OvFlConnSewerN | (Gravity Tanks) Does the overflow have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Overflow on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain. (see photo #) No overflow may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the overflow pipe terminates at least three pipe diameters above the ground level at the sewer or storm drain, or over a splash pad. |
| gvTk5DLAccessblN | (Gravity Tanks) Is the drain accessible for inspection? | Unknown integrity of storage tank drain [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank drain [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk5DLAirGapN | (Gravity Tanks) Does the drain pipe have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Drain on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain*. (see photo #) No drain may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the drain pipe terminates at least three pipe diameters above the ground level at the sewer drain, storm drain, splash pad or engineered rip-rap. |
| gvTk5VentSepN | (Gravity Tanks) Does the tank have a vent separate from the overflow? | No vent on finished water storage tank*. In order to protect the structural integrity of the tank during changes to tank water levels, and other events affecting the confined air space, the tank must have a vent that is separate from the overflow. |
| gvTk5AirVentAccessN | (Gravity Tanks) Is the vent accessible for inspection? | Unknown integrity of storage tank air vent [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank air vent [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. The EPA will review the inspection report and may require additional corrective actions. |
| gvTk5AirVntMeshN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Is there #24-mesh screen? | Air vent screening on finished water storage tank needs improvement*. (see photo #) The vent must be fitted with non-corrodible #24-mesh screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. Prior to installing the screen, the PWS should evaluate whether the tank needs a vacuum/pressure relief valve or another mechanism to prevent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk5AirVnt24AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Downturned vent: Is the vent at least 24“ above the roof? | Downturned air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24” above the tank surface to prevent inhalation of contaminants by the tank. |
| gvTk5AirVentSoldCovN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is there a solid cover down to the bottom of the vent screen? | Air vent on finished water storage tank does not have a solid cover*. (see photo #) For non-downturned vents, the screen must have a solid cover down to the bottom of the vent screen to prevent rain and snow, and minimize dust and sunlight, from entering the tank. If the cover is installed in a manner that restricts the size of the vent opening it may result in insufficient airflow and subsequent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require evaluation by a licensed engineer to ensure that no damage will occur to the existing water tank as a result of the modifications. For elevated tanks and standpipes, the EPA strongly recommends that the system install a vent with an automatic re-setting vacuum/pressure relief mechanism if one is not already in place. |
| gvTk5AirVnt8AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is the screen at least 8” above the roof surface? | Air vent on finished water storage tank is not elevated above the roof at the required height*. (see photo #) For non-downturned vents, the bottom of the vent screen must be at least 8” above the tank roof to prevent inhalation of contaminants by the tank. |
| gvTk5AirVen24MeshN | (Gravity Tanks) Below Ground (buried or partially buried) Is air vent covered with #24-mesh screen? | Air vent screening on finished water storage tank improvement needed*. (see photo #) The vent must be fitted with non-corrodible #24-mesh screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk5AirVnTermDwnN | (Gravity Tanks) Below Ground (buried or partially buried) Does the air vent terminate downward? | Air vent on finished water storage tank does not terminate in a downturned position*. (see photo #) On buried or partially buried tanks the air vent must terminate in a downturned position. |
| gvTk5AirVnTrmAbvRfN | (Gravity Tanks) Below Ground (buried or partially buried) Is the air vent at least 24” above the roof or ground surface (whichever is higher)? | Air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24 inches above the roof or ground surface (whichever is higher) to prevent rain from entering and to prevent inhalation of contaminants by the tank. |
| gvTk5AHAccessableN | (Gravity Tanks) Is the hatch accessible for inspection? | Unknown integrity of storage tank access hatch [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank access hatch [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. The EPA will review the inspection report and may require additional corrective actions. |
| gvTk5bgAH24AboveRfN | (Gravity Tanks) For below ground tanks where the roof is completely buried, is the hatch raised at least 24” above ground level? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the ground surface. |
| gvTk5pbAH24AboveRfN | (Gravity Tanks) For partially buried tanks where the roof is visible, is the hatch raised at least 24” above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the surface of the roof. |
| gvTk5agAH4AboveRfN | (Gravity Tanks) For above ground tanks (ground level or elevated/standpipe): Is the hatch raised 4“ above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be framed at least four inches above the surface of the roof. |
| gvTk5AHShoeBxLidN | (Gravity Tanks) Does the hatch have a shoe box lid? | Hatch on Finished Water Storage Tank does not have a shoe box lid*. (see photo #) The tank hatch must be fitted with a solid watertight cover which extends down around the frame at least two inches. |
| gvTk5AHRubberGaskN | (Gravity Tanks) Is the lid tight and sealed with a rubber gasket? | Hatch on Finished Water Storage Tank does not have a gasket that creates a watertight seal. (see photo #) The tank hatch must have a rubber gasket to seal the hatch lid to the frame tightly to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| gvTk5AHALockedN | (Gravity Tanks) Is the hatch locked? | Hatch on Finished Water Storage Tank does not have a locking device. (see photo #) The cover must have a locking device. |
| gvTk6FloodingY | (Gravity Tanks) Is the site subject to flooding? | Storage tank located in an area subject to flooding. (see photo # ) [insert site specific problem and remedy] |
| gvTk6PropMaintN | (Gravity Tanks) Does the tank appear structurally sound? | Storage tank not structurally sound or properly maintained*. (see photo # ) The storage tank does not appear to be structurally sound. Specifically, the [tank component] of the tank must be evaluated by a professional engineer familiar with the construction of water-storage tanks to determine the integrity of the tank’s [tank component]. Failure to maintain the structural and sanitary integrity of the tank could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank must be made as soon as possible and it must be repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk6FounStrucSoundN | (Gravity Tanks) Does the foundation appear structurally sound? | Storage tank foundation does not appear to be structurally sound*. (see photo # ) The storage tank foundation does not appear to be structurally sound. It must be evaluated by a professional engineer familiar with the construction of water-storage tanks. Failure to maintain the structural and sanitary integrity of the tank foundation could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank foundation must be made as soon as possible and the foundation repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk6OpeningsY | (Gravity Tanks) Are there any unprotected openings in the tank (breaches, leaks, etc)? | Storage tank not sealed*. (see photo #) Other than the openings afforded by the #24-mesh screens on the vents and overflows, all openings must be sealed completely to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. [Describe specific openings such as: All openings between the roof and sidewalls must be sealed and watertight. Any openings from antennas, telemetry, and other appurtenances must be sealed and watertight.] |
| gvTk6InspectedN | (Gravity Tanks) If the tank is more than 10 years old, was it cleaned and inspected within the last 10 years? | Storage tank not cleaned and inspected within the last 10 years. The tank must be cleaned and inspected. Please see the enclosed Finished Water Storage Tank Inspection/Cleaning Checklist for a list of items that must be evaluated during the inspection. Tanks need to be periodically cleaned and inspected to prevent the growth of potentially harmful pathogens in the accumulated sediments and to address construction issues before they require major repairs. Inspections and cleaning may be done by a third-party professional or appropriately trained in-house staff. Please be aware that some tanks may be considered as confined spaces or hazardous environments; personnel working in or near the tanks should have all OSHA-required training, and proper safety equipment and procedures should be used at all times. After inspection and cleaning the tank must be disinfected according to AWWA standards (C652-92: Disinfection of Water Storage Facilities). In order to correct this significant deficiency, you must provide EPA with the following documentation: A completed copy of the Finished Water Storage Tank Inspection/Cleaning Checklist. A copy of inspection results and labeled photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk6OvFlSepN | (Gravity Tanks) Does the tank have an overflow separate from the vent? @ | No overflow on finished water storage tank*. In order to protect the integrity of the tank in the case of control system failure leading to overfilling, the tank must have an overflow that is separate from the vent. |
| gvTk6OvFlAccessN | (Gravity Tanks) Is the overflow accessible for inspection? | Unknown integrity of storage tank overflow [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank overflow [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk6OvFl24MeshN | (Gravity Tanks) Overflow has a #24-mesh screen OR a duckbill valve OR a properly sealed flapper valve with screen inside (the EPA recommends a #24-mesh screen)? | Overflow screening on finished water storage tank improvement needed*. (see photo #) Overflows must be fitted with non-corrodible #24-mesh screen, or a properly sealed flapper or duckbill valve to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the pipe at a location least susceptible to vandalism. When a flapper valve is used, a screen must be placed inside the valve (EPA Region 8 recommends non-corrodible #24-mesh screen be used). In cold climates, use of a flapper or duckbill valve should be considered to minimize air movement and hence ice formation in the tank. In cold climates, provisions should be considered to prevent the flapper or duckbill from freezing shut. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk6OvFlTerm12InN | (Gravity Tanks) Does the overflow line terminate no less than 12 inches but no more than 24 inches above the ground surface? | Overflow on finished water storage tank discharges at improper height*. (see photo #) Overflow must be piped to an elevation between 12 and 24 inches above the ground surface and discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk6OvDrainStructN | (Gravity Tanks) Does the overflow discharge over an inlet structure, splash plate, or engineered rip-rap? | Overflow discharge point on finished water storage tank improvement needed*. (see photo #) Overflow must discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk6OvFlConnSewerN | (Gravity Tanks) Does the overflow have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Overflow on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain. (see photo #) No overflow may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the overflow pipe terminates at least three pipe diameters above the ground level at the sewer or storm drain, or over a splash pad. |
| gvTk6DLAccessblN | (Gravity Tanks) Is the drain accessible for inspection? | Unknown integrity of storage tank drain [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank drain [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk6DLAirGapN | (Gravity Tanks) Does the drain pipe have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Drain on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain*. (see photo #) No drain may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the drain pipe terminates at least three pipe diameters above the ground level at the sewer drain, storm drain, splash pad or engineered rip-rap. |
| gvTk6VentSepN | (Gravity Tanks) Does the tank have a vent separate from the overflow? | No vent on finished water storage tank*. In order to protect the structural integrity of the tank during changes to tank water levels, and other events affecting the confined air space, the tank must have a vent that is separate from the overflow. |
| gvTk6AirVentAccessN | (Gravity Tanks) Is the vent accessible for inspection? | Unknown integrity of storage tank air vent [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank air vent [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. The EPA will review the inspection report and may require additional corrective actions. |
| gvTk6AirVntMeshN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Is there #24-mesh screen? | Air vent screening on finished water storage tank needs improvement*. (see photo #) The vent must be fitted with non-corrodible #24-mesh screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. Prior to installing the screen, the PWS should evaluate whether the tank needs a vacuum/pressure relief valve or another mechanism to prevent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk6AirVnt24AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Downturned vent: Is the vent at least 24“ above the roof? | Downturned air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24” above the tank surface to prevent inhalation of contaminants by the tank. |
| gvTk6AirVentSoldCovN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is there a solid cover down to the bottom of the vent screen? | Air vent on finished water storage tank does not have a solid cover*. (see photo #) For non-downturned vents, the screen must have a solid cover down to the bottom of the vent screen to prevent rain and snow, and minimize dust and sunlight, from entering the tank. If the cover is installed in a manner that restricts the size of the vent opening it may result in insufficient airflow and subsequent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require evaluation by a licensed engineer to ensure that no damage will occur to the existing water tank as a result of the modifications. For elevated tanks and standpipes, the EPA strongly recommends that the system install a vent with an automatic re-setting vacuum/pressure relief mechanism if one is not already in place. |
| gvTk6AirVnt8AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is the screen at least 8” above the roof surface? | Air vent on finished water storage tank is not elevated above the roof at the required height*. (see photo #) For non-downturned vents, the bottom of the vent screen must be at least 8” above the tank roof to prevent inhalation of contaminants by the tank. |
| gvTk6AirVen24MeshN | (Gravity Tanks) Below Ground (buried or partially buried) Is air vent covered with #24-mesh screen? | Air vent screening on finished water storage tank improvement needed*. (see photo #) The vent must be fitted with non-corrodible #24-mesh screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk6AirVnTermDwnN | (Gravity Tanks) Below Ground (buried or partially buried) Does the air vent terminate downward? | Air vent on finished water storage tank does not terminate in a downturned position*. (see photo #) On buried or partially buried tanks the air vent must terminate in a downturned position. |
| gvTk6AirVnTrmAbvRfN | (Gravity Tanks) Below Ground (buried or partially buried) Is the air vent at least 24” above the roof or ground surface (whichever is higher)? | Air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24 inches above the roof or ground surface (whichever is higher) to prevent rain from entering and to prevent inhalation of contaminants by the tank. |
| gvTk6AHAccessableN | (Gravity Tanks) Is the hatch accessible for inspection? | Unknown integrity of storage tank access hatch [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank access hatch [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. The EPA will review the inspection report and may require additional corrective actions. |
| gvTk6bgAH24AboveRfN | (Gravity Tanks) For below ground tanks where the roof is completely buried, is the hatch raised at least 24” above ground level? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the ground surface. |
| gvTk6pbAH24AboveRfN | (Gravity Tanks) For partially buried tanks where the roof is visible, is the hatch raised at least 24” above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the surface of the roof. |
| gvTk6agAH4AboveRfN | (Gravity Tanks) For above ground tanks (ground level or elevated/standpipe): Is the hatch raised 4“ above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be framed at least four inches above the surface of the roof. |
| gvTk6AHShoeBxLidN | (Gravity Tanks) Does the hatch have a shoe box lid? | Hatch on Finished Water Storage Tank does not have a shoe box lid*. (see photo #) The tank hatch must be fitted with a solid watertight cover which extends down around the frame at least two inches. |
| gvTk6AHRubberGaskN | (Gravity Tanks) Is the lid tight and sealed with a rubber gasket? | Hatch on Finished Water Storage Tank does not have a gasket that creates a watertight seal. (see photo #) The tank hatch must have a rubber gasket to seal the hatch lid to the frame tightly to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| gvTk6AHALockedN | (Gravity Tanks) Is the hatch locked? | Hatch on Finished Water Storage Tank does not have a locking device. (see photo #) The cover must have a locking device. |
| swEpichlorohidrinY | (SW Treatment) Does the system use a chemical containing epichlorohydrin or polyacrylamide that is dosed in excess of the NSF 60 Max Allowable Dose? | System has a potential violation for excess dosing of a chemical that contains epichlorohydrin or polyacrylamide (141.111). |
| filtPrLocationEPAN | (SW Treatment) Does the location of the CFE turbidimeter comply with EPA policy SWTR #5? | Combined Filter Effluent (CFE) turbidity monitoring location is not representative of the filtered water*. The system’s finished water (CFE) turbidimeter sampling location is not representative of the filtered water. [describe system specific situation and remedy] |
| swTurbimCalibrateN | (SW Treatment) Are turbidimeters calibrated at least once every quarter? | Turbidimeters Must Be Calibrated Quarterly. Turbidity is used to measure filtration effectiveness, and incorrect turbidity monitoring has the potential to allow contamination to pass into the finished water. The Long Term 1 Enhanced Surface Water Treatment Rule requires that turbidimeter calibration be conducted using procedures specified by the manufacturer. To be consistent with typical manufacturer specifications for surface water treatment plants, turbidimeters for measuring individual filter effluent (IFE) and combined filter effluent (CFE) turbidity must be calibrated at least quarterly according to manufacturer procedures using a primary standard such as formazin. |
| swPrimaryStndCalibrN | (SW Treatment) Does the system use a primary standard to perform the calibration? | Primary Standard Not Used to Calibrate Turbidimeters. Turbidity is used to measure filtration effectiveness, and incorrect turbidity monitoring has the potential to allow contamination to pass into the finished water. The Long Term 1 Enhanced Surface Water Treatment Rule requires that turbidimeter calibration be conducted using procedures specified by the manufacturer. To be consistent with typical manufacturer specifications for surface water treatment plants, turbidimeters for measuring individual filter effluent (IFE) and combined filter effluent (CFE) turbidity must be calibrated at least quarterly according to manufacturer procedures using a primary standard such as formazin. |
| swPotVioTurbRecN | (SW Treatment) Are CFE turbidity records available for the last 5 years? | System has a potential violation for failing to maintain CFE turbidity records (141.33a). |
| filtPrRec5NTUN | (SW Treatment) Can CFE turbidities be recorded up to 5 NTU? | Inadequate treatment process monitoring, recording, and recordkeeping for surface water treatment plants. The SCADA system must be able to record and store combined filter effluent (CFE) turbidity values up to at least 5 NTU. |
| filtPrBkWshTurbIdntN | (SW Treatment) (Conventional and Direct) Can turbidities associated with off-periods (backwash, FTW) be identified so they are not counted for compliance? | Inadequate Treatment Process Monitoring, Recording, and Recordkeeping for Surface Water Treatment Plants. The IFE turbidity recording method employed by the system does not adequately identify the status of the filter at the time each turbidity reading is recorded (i.e. filtering to clearwell, backwashing, filtering to waste, offline). As a result, the surveyor was not able to determine which turbidity values were valid readings that counted toward compliance. |
| convDirF24InchN | (SW Treatment) (Conventional and Direct) Total at least 24”? | Inadequate filtration design or operation. During the survey, the operators indicated that the depth of the filtration media is insufficient. The 2012 Recommended Standards for Water Works (10 States Standards) Section 4.3.1.6 Filter Material states that filter media depth for rapid sand filtration should not be less than 24 inches. |
| convDirFRateLT2gpmN | (SW Treatment) (Conventional and Direct) Is the filtration rate less than 2 gpm/sf (mono-media), 4 gpm/sf (dual media) or 6 gpm/sf (deep bed)? | Inadequate treatment process operations. Operations at the water treatment plant create the potential for sending inadequately treated water to distribution. The current operation of the filter exceeds the recommended loading rate. |
| convDirFBckWshRaw | (SW Treatment) (Conventional and Direct) What is used for a backwash? raw water | System is using raw water to backwash conventional or direct filters that are the system's final filtration barrier. (no standard language) |
| convDirFTMTurbConN | (SW Treatment) (Conventional and Direct) Does each filter have an individual effluent (IFE) turbidimeter? | System has a potential violation for failing to monitor the IFE turbidity as required by the regulations for conventional / direct filtration plants (141.560 or 141.174a)*. |
| convDirAdRecRdgN | (SW Treatment) (Conventional and Direct) Are IFE turbidities measured continuously, and recorded at least every 15 Minutes | System has a potential violation for failing to adequately record the IFE turbidity readings as required by the regulations for conventional / direct filtration plants (141.560c or 141.174a). |
| convDirIFECalibrateN | (SW Treatment) (Conventional and Direct) Is IFE turbidity recorder (SCADA or charts) calibrated to record turbidities ≥ 2 NTU? | Inadequate Treatment Process Monitoring, Recording, and Recordkeeping for Surface Water Treatment Plants The Long Term 1 Enhanced Surface Water Treatment Rule requires that the turbidity of the finished water from the individual filters be monitored continuously and recorded at least once every 15 minutes. This data is used to determine whether an individual filter effluent (IFE) turbidity exceeds either 1.0 or 2.0 NTU in two consecutive 15 minute readings, which may trigger the need for corrective actions. The IFE turbidimeters must be calibrated to record turbidity values of at least 2.0 NTU. |
| convDirFToMntIFEN | (SW Treatment) (Conventional and Direct) Are IFE records kept for the last 3 years (as applicable)? | System has a potential violation for failing to maintain IFE records for 3 years (conventional and direct filtration) (141.571a or 141.175b). |
| convDirFToRptIFETrbN | (SW Treatment) (Conventional and Direct) If so, did they report to the EPA and do a filter profile, if required? | System has a potential violation for failing to report high IFE turbidities to the EPA and conduct a filter profile (141.175b1). |
| convDirFTRSelfAssN | (SW Treatment) (Conventional and Direct) If this occurred 3 months in a row, did they conduct a filter self-assessment? | System has a potential violation for failing to report high IFE turbidity readings to the EPA and conduct a filter self-assessment following 3 months of IFE turbidity readings over 1 NTU (141.563b or 141.175b3). |
| convDirFTR2NTUN | (SW Treatment) (Conventional and Direct) If this occurred 2 months in a row for the same filter, did they report to the EPA and have a CPE performed? | System has a potential violation for failing to report to the EPA and have a CPE performed following 2 months of IFE turbidity readings over 2 NTU (141.563c or 141.175b4). |
| convDirFTRGT10KN | (SW Treatment) (Conventional and Direct) If so, did they report to the EPA and do a filter profile, if required? | System has a potential violation for failing to report high IFE turbidities to the EPA and conduct a filter profile (IESWTR - systems greater than 10,000) (141.175b2). |
| convDirExdCFELimN | (SW Treatment) (Conventional and Direct) Based on these records, has the system consistently met the CFE turbidity requirements for this type of filtration during the last 12 months? | System has a potential violation for exceeding the CFE turbidity limits for conventional or direct filtration and failing to report to the EPA (141.551a1 / 141.551b1 or 141.173a / 141.173a2). |
| convDirFTMBckWshN | (SW Treatment) (Conventional and Direct) Are records of recycle practices kept in an acceptable format for each year that includes all of the required elements? | System has a potential violation for failing to maintain the records required by the Filter Backwash Recycling Rule (141.76). |
| conDirExdTurMemN | (SW Treatment) (Membranes) Has the PWS consistently been meeting the CFE turbidity requirements for this type of filtration? | System has a potential violation for exceeding the CFE turbidity limits for membrane filtration and failing to report to the EPA (141.551a2 / 141/551b2 or 141.173b). |
| convDirDITMemN | (SW Treatment) (Membranes) Are direct integrity tests (DIT) performed at least daily (specify pressure or vacuum applied)? | Inadequate Membrane Filtration Operation resulting in Inadequate Treatment (this is a violation of 141.719b3 for systems that receive credit for additional filtration under the LT2ESWTR): Due to plant design and / or equipment problems, direct integrity tests (DIT) are not being performed on all membrane skids on a daily basis. Daily direct integrity testing is required to evaluate whether there are breaches in the membrane modules which would allow contamination to pass through to the filtered water. Membrane units that are not being assessed for integrity by daily direct integrity testing are considered cartridge filtration rather than membrane filtration. Cartridge filters are credited with only 2 logs removal of Giardia rather than the 3 logs Giardia removal credited to membrane filtration. To meet the treatment technique for 3 logs Giardia reduction of 40 CFR §141.70(a)(1) of the Surface Water Treatment Rule, cartridge filtration systems must achieve an additional 1.0 log inactivation of Giardia. As documented in the sanitary survey, under winter conditions the plant disinfection process is not able to achieve 1.0 log inactivation of Giardia at the first user. Therefore, the system must resume conducting and passing daily direct integrity tests on both membrane skids to receive the higher Giardia removal credits associated with membrane filtration. |
| convDirInadFilDesN | (SW Treatment) (Membranes) For continuous indirect integrity testing, does each unit/skid have its own online turbidimeter | Inadequate Filtration Design or Operation, resulting in Inadequate Treatment* (this is a violation of 141.719b4 for systems that receive credit for additional filtration under the LT2ESWTR): The individual membrane filtration units are not equipped with a turbidimeter that continuously samples the individual filter effluent (IFE). Membrane units that do not (1) have an individual filter turbidimeter, and (2) are not continuously monitoring turbidity from each unit with a 0.15 NTU trigger for repeat direct integrity testing, are considered cartridge filtration rather than membrane filtration. Cartridge filters are credited with only 2 logs removal of Giardia rather than the 3 logs Giardia removal credited to membrane filtration. To meet the treatment technique for 3 logs Giardia reduction of 40 CFR §141.70(a)(1) of the Surface Water Treatment Rule, cartridge filtration systems must achieve an additional 1.0 log inactivation of Giardia. As documented in the sanitary survey, the plant disinfection process does not consistently achieve 1.0 log inactivation of Giardia at the first user. Therefore, the system must install an IFE turbidimeter on each membrane unit that triggers an integrity test when the turbidity exceeds 0.15 NTU in order to receive the higher Giardia removal credits associated with membrane filtration. |
| convDirIFEMon15N | (SW Treatment) (Membranes) Is filtrate turbidity monitored continuously and recorded at least once every15 minutes? | System has a potential violation for not monitoring IFE continuously and recording values once every 15 minutes (membrane filtration) (141.719b4) (systems not receiving additional filtration credit under the LT2ESWTR - considered a significant deficiency). (no standard language) |
| convDirIFETurTr15N | Is it set with a trigger level of 0.15 NTU for > 15 minutes (a DIT should be initiated when filtrate turbidity exceeds this level)? | System has a potential violation - IFE turbidimeters not set with a trigger level of 0.15 NTU for longer than 15 minutes to initiate a DIT (membrane filtration) (141.719b4) (systems not receiving additional filtration credit under the LT2ESWTR - considered a significant deficiency). (no standard language) |
| membrOpKwChkMembrN | (SW Treatment) (Membranes) Do operators know how to check and repair membranes when a DIT fails? | System operators do not know how to check and repair membranes if a direct integrity test fails. (no standard language) |
| bgsCartExdTurbLimN | (SW Treatment) (Bags and Cartridges) Has the PWS consistently been meeting the CFE turbidity requirements for this type of filtration? | System has a potential violation for exceeding the CFE turbidity limits for bag / cartridge filtration and failing to report to the EPA (141.551a2 / 141/551b2 or 141.173b) |
| bgsCartPressGaugeN | (SW Treatment) (Bags and Cartridges) Are there working pressure gauges before and after filters? | Inadequate filtration design or operation*. Adequate microbial removal requires that a cartridge system not be used at conditions exceeding its design specifications (flow rate, inlet pressure and pressure drop), and that the cartridge be properly installed in the housing for which it was designed. The current treatment system does not have flowmeters or flow restrictors, nor pressure gauges to monitor pressure drop across the cartridges. It is unclear what the system design limitations are. The filter housings and cartridge elements should be evaluated to ensure that manufacturer’s recommended flow and pressure limits are not exceeded; flowmeters and flow restrictors should be installed as needed if the filters are not designed for the maximum flow from the intake pumps. Pressure gauges should be installed up and downstream of the cartridges to allow daily monitoring and recording of pressure drops and to trigger filter change outs when manufacturer’s limits are close to being reached. |
| bgsCartRecPressDrpN | (SW Treatment) (Bags and Cartridges) Does the PWS keep daily records of monitoring the pressure drop across the filters, and know when to change out filters? | Inadequate filtration design or operation. Adequate microbial removal requires that a cartridge system not be used at conditions exceeding its design specifications (flow rate, inlet pressure and pressure drop), and that the cartridge be properly installed in the housing for which it was designed. In order to ensure that these conditions are met, the differential pressure across the filter bags should be monitored and recorded daily and the filters should be changed out when the manufacturer’s limits are close to being reached. The system is currently not monitoring and / or recording these values on a daily basis. |
| bgsCartRemvCrytoN | (SW Treatment) (Bags and Cartridges) Has the final filter or pre/final filter combination been demonstrated to remove at least 99.9% of Cryptosporidium or equivalent size particles or have a 1 or 2 micron absolute pore size rating? | Inadequate filtration design or operation*. In order to ensure 99% removal of Cryptosporidium as required by the Long Term 1 Enhanced Surface Water Treatment Rule, the final cartridge filter must be one to two micron absolute pore size, unless the manufacturer can provide challenge testing results showing 99.9% removal of Cryptosporidium or a surrogate of the same size. According to the manufacturer, the bag filter currently being used as the final filtration barrier has not been certified for Cryptosporidium removal. The PWS should provide documentation indicating that the existing filter meets the above requirements, or use a different filter that does meet these requirements. |
| bgsCartFlowExceedY | (SW Treatment) (Bags and Cartridges) Does the flow rate through the final filter exceed the manufacturer’s maximum recommended flow rate? | Inadequate filtration design or operation*. The bag filter currently being used as the final filtration barrier is being operated at a rate that exceeds the manufacturer’s recommended maximum flow rate. Adequate microbial removal requires that a cartridge system not be used at conditions exceeding its design specifications (flow rate, inlet pressure and pressure drop). |
| bgsCartDEFilTurbN | (SW Treatment) (DE Filtration) Has the PWS consistently been meeting the CFE turbidity requirements for this type of filtration? | System has a potential violation for exceeding the CFE turbidity limits for DE filtration and failing to report to the EPA (141.551a2 / 141/551b2 or 141.173b). |
| ditEaFRateN | (SW Treatment) (DE Filtration) Is the filtration rate less than 1.5 gpm/sf? | The Diatomaceous Earth filters are being operated at a rate that exceeds 1.5 gpm/sf. (no standard language) |
| slwSndFilRateN | (SW Treatment) (Slow Sand) Is the filtration rate less than 0.1 gpm/sf? | The slow sand filters are being operated at a rate that exceeds 0.1 gpm/sf. (no standard language) |
| slwSndExdTurbLN | (SW Treatment) (Slow Sand) Has the PWS consistently been meeting the CFE turbidity requirements for this type of filtration? | System has a potential violation for exceeding the CFE turbidity limits for slow sand filtration and failing to report to the EPA (141.551a2 / 141/551b2 or 141.173b) |
| slwSndRwTurbLT10N | (SW Treatment) (Slow Sand) Is turbidity of raw water to filters always <10 NTU? | The slow sand filters are being used to treat raw water that exceeds 10 NTU. (no standard language) |
| slwSndDepthOSand3FtN | (SW Treatment) (Slow Sand) Is water depth over sand at least 3 feet during operation? | The depth of the water being maintained at the slow sand filters is less than 3 feet during operation. (no standard language) |
| slwSndHeadLossMonN | (SW Treatment) (Slow Sand) Is head loss across filters monitored and used for process control? | The system is using slow sand filters as a final filtration barrier and not monitoring the head loss for process control. (no standard language) |
| slwSndFTMUVRecN | (SW Treatment) (UV Disinfection) Does PWS keep records of UV reports sent monthly to the EPA? | System has a potential violation for failing to maintain UV operation records (141.722c) |
| uvDisFlowMeterAlarmN | (SW Treatment) (UV Disinfection <40 gpm) Is there a flow meter to monitor/alarm or a flow restrictor valve so the max flow rate is not exceeded | The system does not have a means of ensuring that the flow rate through the UV unit does not exceed the manufacturer’s maximum validated flow rate (less than 40 gpm UV). (no standard language) |
| uvDisIntensitySensN | (SW Treatment) (UV Disinfection <40 gpm) Is there an intensity sensor and alarm (visible/audible) to indicate low intensity? | The system does not have an intensity sensor alarm to indicate low UV intensity (less than 40 gpm UV). (no standard language) |
| uvDisUVStatusAlmN | (SW Treatment) (UV Disinfection <40 gpm) Is there a UV lamp status alarm (visible/audible) to indicate lamps off | The system does not have a UV lamp status alarm (less than 40 gpm UV). (no standard language) |
| uvDisLampAgeAlmN | (SW Treatment) (UV Disinfection <40 gpm) Is there a UV lamp age counter/alarm? | The system does not have a UV lamp age counter / alarm (less than 40 gpm UV). (no standard language) |
| uvDisAutoShutOffN | (SW Treatment) (UV Disinfection <40 gpm) Is there an automatic shut-off fail-safe solenoid valve so that water does not flow through the unit without adequate treatment? | The UV disinfection unit is not equipped with a fail safe solenoid valve*. A fail safe solenoid valve that shuts off flow through the units when an adequate UV dose is not being achieved must be installed. |
| uvDisNSFStndCertN | (SW Treatment) (UV Disinfection <40 gpm) Does this UV unit have an NSF Standard 55A Certification or has it been validated according to the requirements of the 2006 UV Disinfection Guidance Manual? | The system has a potential violation. The UV unit being used by the system for Cryptosporidium inactivation credit does not have the required NSF 55A Certification (less than 40 gpm UV) or validation according to the UVDGM / DVGW (greater than 40 gpm UV). |
| uvDisLT40SensCaliN | (SW Treatment) (UV Disinfection >40 gpm) Is the calibration of the UV intensity sensors checked at least monthly using a reference sensor | The system does not check the calibration of their UV intensity sensors at least monthly. As a system that utilizes UV disinfection to achieve Cryptosporidium inactivation credit to meet the requirements of the Long Term 2 Enhanced Surface Water Treatment Rule, you are required to verify the calibration of all UV sensors monthly and recalibrate the sensors if they do not meet the quality control requirements specified in the EPA UV Disinfection Guidance Manual. The system currently does not conduct UV intensity sensor calibration verifications. The system must work with the UV unit manufacturer to begin performing and documenting monthly UV intensity sensor calibration verifications on all UV units. If any UV sensor does not meet the quality control requirements specified in the UV Disinfection Guidance Manual, it must be recalibrated. |
| uvDisLT40TrnsmCalibN | (SW Treatment) (UV Disinfection >40 gpm) Is the calibration of the UV transmittance analyzer checked at least weekly with a benchtop analyzer (Calculated Dose Method only)? | The system does not check the calibration of their online UV transmittance analyzer on a weekly basis. As a system that utilizes UV disinfection to achieve Cryptosporidium inactivation credit to meet the requirements of the Long Term 2 Enhanced Surface Water Treatment Rule, you are required to continuously monitor the finished water UV transmittance. This parameter is a primary input into the calculated dose equation used to demonstrate that adequate inactivation is being achieved. The system currently does not conduct UV transmittance analyzer calibration verifications. The system must begin conducting weekly verification of the online UVT analyzer using a grab sample. |
| uvDisLT40CalibFlowMN | (SW Treatment) (UV Disinfection >40 gpm) Is there a calibrated flowmeter to ensure max flow rate is not exceeded? | The system currently does not have a calibrated flow meter on one or more of the UV disinfection units*. As a system that utilizes UV disinfection to achieve Cryptosporidium inactivation credit to meet the requirements of the Long Term 2 Enhanced Surface Water Treatment Rule, you are required to monitor the flow rate at each UV unit to ensure that the units are being operated within the validated conditions. Currently, the flow meter at one or more of the UV units is inoperable. The system must repair all flow meters as necessary to allow for direct monitoring of the flow rate at each UV unit. |
| uvdisFTMRecs40N | (SW Treatment) (UV Disinfection >40 gpm) Are daily operational records kept of flow rates/production, run time, lamp status, UV intensity, UVT and UV dosage? | System has a potential violation for failing to maintain UV operation records (greater than 40 gpm UV) (141.720d5). |
| uvDisLT40OperIDEvntN | (SW Treatment) (UV Disinfection >40 gpm) Does the operator know how to identify an off-specification event and report it to the EPA? | The system operators do not know how to properly identify an off-specification event and report it to the EPA (greater than 40 gpm UV). (no standard language) |
| uvDisLT40SysAlarmEvN | (SW Treatment) (UV Disinfection >40 gpm) Does the system alarm when an off-specification event occurs? | The plant's SCADA is not set up to alarm when an off-specification event occurs (greater than 40 gpm UV)*. (no standard language) |
| uvDisFTMPoeRsdN | (SW Treatment) (Chlorination) Is this before the 1st user of the water? | System has a potential violation for monitoring the POE chlorine residual at a point that is not prior to the first user of the water (141.74c2). |
| chmDis2MsmtN | (SW Treatment) (Chlorination) Are the two measurements within 0.1 mg/L or 15% of one another (whichever is larger)? | Inadequate Treatment Process Monitoring for Surface Water Treatment Plants. The online chlorine residual analyzer at the point of entry was not adequately calibrated and periodically verified. The chlorine residual at the point of entry measured by the surveyor using a handheld DPD device varied substantially from the reading by the online analyzer. According to EPA Method 334.0: Determination of Residual Chlorine in Drinking Water Using an On-Line Chlorine Analyzer; during routine calibration checks of the online analyzer, the continuous analyzer chlorine residual reading must be within 0.1 mg/L or 15% (whichever is greater) of the grab sample measurement. If the readings are outside of this range, follow-up calibration procedures are required. The following actions must be taken: a. The online analyzer should be calibrated per manufacturer’s specifications and then checked with a grab sample taken at the same location (using an accurate handheld DPD analyzer) to ensure that the variance is within the specified limits. If after calibration the device still does not meet the above requirements, the system should contact the manufacturer to troubleshoot the problem and calibrate the instrument. b. The online analyzer should be verified with a grab sample once every seven days and records of the verifications kept in the operating logs. If the variance between the two readings is ever outside of the specified limits (0.1 mg/L or 15%, whichever is larger), the online chlorine residual analyzer should be calibrated and re-checked. If this does not bring the readings within the specified limits, the system should contact the manufacturer to troubleshoot the problem. |
| chmDisMeaResidContN | (SW Treatment) (Chlorination) If measuring residual continuously, is the PWS conducting weekly verifications with a grab sample measurement? | Inadequate Treatment Process Monitoring, Recording, and Recordkeeping for Surface Water Treatment Plants. The online chlorine residual analyzer at the point of entry to the distribution system was not periodically verified to determine the need for calibration per the requirements of EPA Method 334.0: Determination of Residual Chlorine in Drinking Water Using an On-Line Chlorine Analyzer. The online analyzer must be verified with a grab sample once every seven days and records of the weekly verifications kept in the operating logs. The continuous analyzer chlorine residual reading must be within 0.1 mg/L or 15% (whichever is greater) of the grab sample measurement. If the readings are outside of this range, follow-up calibration procedures are required. |
| chmDisFTMBromaN | (SW Treatment) (Ozonation) Does the system monitor bromate concentration at point of entry? | System has a potential violation for failing to monitor bromate at the point of entry according to the required frequency (system using ozone) (141.132b3). |
| chmDisFTMClDioxN | (SW Treatment) (Chlorine Dioxide) Does the system monitor chlorine dioxide daily at point of entry? | System has a potential violation for failing to monitor chlorine dioxide at the point of entry according to the required frequency (system using chlorine dioxide) (141.132c2). |
| chmDisFTMChloritN | (SW Treatment) (Chlorine Dioxide) Does the system monitor chlorite at point of entry daily and monthly in the distribution system? | System has a potential violation for failing to monitor chlorite at the point of entry according to the required frequency (system using chlorine dioxide) (141.132b2). |
| chmDis1YrProfNCmN | (SW Treatment) (Disinfection Profiling) Does the system have a disinfection profile on site that contains a year of weekly log inactivation calculations (<10,000 pop.) or a year of daily log inactivation calculations (>10,000 pop)? | One year disinfection profile not completed. This public water system was required to conduct one year of disinfection profiling as part of the Long Term 1 Enhanced Surface Water Treatment Rule. The disinfection profile consists of inactivation calculations for Giardia and viruses calculated once per week over a year’s time. During this sanitary survey, a complete one year profile was not available for review. The system must collect information on the plant’s flow rate, contact tank volume, pH, temperature, and chlorine residual on at least a weekly basis to calculate Giardia and virus inactivation levels for one year. This information should be used to complete the required one year disinfection profile and the profile should then be kept in the plant’s records indefinitely. Failure to have the profile available for review during sanitary surveys is a recordkeeping violation of 40 C.F.R. §141.536. |
| chmDisFTConsultN | (SW Treatment) (Disinfection Profiling) If yes, was the EPA consulted? | System has a potential violation for failing to consult the EPA prior to making a significant change to their disinfection practices (141.570d or 141.172c). |
| virGiVGt4RmvN | (SW Treatment) (Overall Removal Virus) > 4 logs? | Inadequate inactivation design or operation (CT)*. The Surface Water Treatment Rule requires that water systems achieve at least 99.99% (4-log) removal and/or inactivation of viruses. The cartridge filtration system employed is not credited with any virus removal due to the large size of the pores in comparison with the size of viruses. In addition, the UV system is not credited with virus inactivation due to the relatively high UV resistance of viruses. The system must therefore achieve 99.99% inactivation of viruses through chemical disinfection. Based upon calculations made in this sanitary survey using conservative values, the required level of virus inactivation is not achieved by the time the water reaches the first user. The system must ensure adequate inactivation; the disinfection profiling spreadsheet sent to the system should be used weekly for one year to document adequate inactivation. If the system is unable to achieve the required 4 log inactivation by adjusting the flow rate or chlorine residual, it is possible that modifications to the system design will be necessary. |
| virGiGt3RmvN | (SW Treatment) (Overall Removal Giardia) > 3 logs? | Inadequate inactivation design or operation (CT)*. The water treatment system operation and/ or design does not provide for adequate inactivation of Giardia lamblia. The SWTR requires that water systems achieve at least 99.9% (3-log) removal and/or inactivation of Giardia lamblia cysts and 99.99% (4-log) removal and/or inactivation of viruses. As documented in this sanitary survey, the filtration system when properly operated does not achieve the required reduction of Giardia; therefore, the system must achieve additional reduction of Giardia through inactivation. The system does not routinely collect and record the data necessary to determine the level of inactivation. Inactivation calculations made based on data collected during the sanitary survey and standard conservative estimates for peak hourly flows and tank and pipeline volumes indicated that the system was not obtaining enough Giardia inactivation to achieve a total reduction (removal plus inactivation) of 99.9%. The system must ensure adequate Giardia reduction; the disinfection profiling spreadsheet provided to the water system should be used weekly to document that the inactivation necessary to achieve the required total reduction of Giardia is achieved. A completed copy must be provided to EPA to show that this significant deficiency has been resolved. If the system is unable to obtain the required inactivation, the system should be modified to increase the level of inactivation (i.e. installation of a second method of inactivation or installation of additional storage to increase contact time). |
| InCryptoInacN | (SW Treatment) (Overall Removal Cryptosporidium) > required logs? | System has a potential violation for failing to maintain adequate treatment for Cryptosporidium as required in the LT2 rule (Bins 2 or higher system or system that committed to install maximum treatment) (141.711a).* |
| disDat20PSIN | (Distribution) Is there at least 20 psi at all points in the system at all times? | Low pressure or loss of pressure (less than 20 psi)*. Presently, some areas of the distribution system have pressure less than 20 psi. This low pressure creates significant risk for backflow and system contamination. In order to correct this significant deficiency, you must identify the cause(s) of the low pressure and provide documentation of how it was corrected. |
| disDatbulkrpz1N | (Distribution) Bulk Water Supply / Fill Station Appropriate Air Gap or RPZ? | Inadequate backflow prevention on [insert station name] bulk water fill station*. (See photo #) Bulk water fill stations present a potential cross-connection. Cross-connections provide a pathway for contamination to enter the drinking water system during backflow events and therefore present a potential public health threat. A reduced pressure backflow assembly (RPZ) or permanent air gap device must be installed at this facility. An RPZ must be inspected and tested at least annually to ensure proper function. For corrective actions refer to WY DEQ Chapter 12 Section 14(i) regulations on Cross Connections. |
| disDatbulkrpz2N | (Distribution) Bulk Water Supply / Fill Station Appropriate Air Gap or RPZ? | Inadequate backflow prevention on [insert station name] bulk water fill station*. (See photo #) Bulk water fill stations present a potential cross-connection. Cross-connections provide a pathway for contamination to enter the drinking water system during backflow events and therefore present a potential public health threat. A reduced pressure backflow assembly (RPZ) or permanent air gap device must be installed at this facility. An RPZ must be inspected and tested at least annually to ensure proper function. For corrective actions refer to WY DEQ Chapter 12 Section 14(i) regulations on Cross Connections. |
| disDatbulkrpz3N | (Distribution) Bulk Water Supply / Fill Station Appropriate Air Gap or RPZ? | Inadequate backflow prevention on [insert station name] bulk water fill station*. (See photo #) Bulk water fill stations present a potential cross-connection. Cross-connections provide a pathway for contamination to enter the drinking water system during backflow events and therefore present a potential public health threat. A reduced pressure backflow assembly (RPZ) or permanent air gap device must be installed at this facility. An RPZ must be inspected and tested at least annually to ensure proper function. For corrective actions refer to WY DEQ Chapter 12 Section 14(i) regulations on Cross Connections. |
| disDatARVLeakY | (Distribution) Do any (ARVs) have leaks and/or standing water that covers the discharge point? | Air relief valve (ARV) vault contains standing water (see photo #) An ARV vault near [describe location] contained standing water from ground water intrusion or leaks in the pipes or valves. Standing water at the discharge point of the air relief valve could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. |
| crsConnRedPrsBckN | (Cross Connection Control) Does each severe hazard connection have the appropriate reduced pressure backflow assembly installed at the meter/service connection and approved air gap (twice the size of the supply pipe diameter but always greater than one inch)? | Unprotected, severe hazard cross-connection present*. (See photo #) (see examples listed below) Cross-connections provide a pathway for contamination to enter the drinking water system during backflow events and therefore present a potential public health threat. The survey identified [specify the cross connection found during the survey] as a severe hazard cross connection. A reduced pressure backflow assembly and air gap that is twice the size of the supply pipe diameter but always greater than one inch must be installed at the service connection to this facility and must be inspected and tested at least annually to ensure proper function. For corrective actions refer to WY DEQ Chapter 12 Section 14(i) regulations on Cross Connections. |
| crsConnAirGapN | (Cross Connection Control) Does each high hazard connection in the treatment plant or distribution system have the appropriate air gap or reduced pressure backflow assembly installed? | Unprotected, high hazard cross-connection present*. (See photo #) (see examples listed below) Cross-connections provide a pathway for contamination to enter the drinking water system during backflow events and therefore present a potential public health threat. The survey identified [specify the cross connection found during the survey] as a high hazard cross connection. A reduced pressure backflow assembly (RPZ) or air gap must be installed at the service connection to this facility. An RPZ must be inspected and tested at least annually to ensure proper function. For corrective actions refer to WY DEQ Chapter 12 Section 14(i) regulations on Cross Connections. |
| crsConnLeakCompY | (Cross Connection Control) Were there any leaking system components observed by the surveyor that are not previously noted? | Leaking system components were identified [describe type and location]. [Describe potential concern and remedy] |
| crsConnStckTnkAirGpN | (Cross Connection Control) (non-community systems only) Stock tanks – approved air gap or atmospheric vacuum breaker at the tank? | Unprotected, high hazard cross-connection present*. (See photo #)(see examples listed below) For Noncommunity Systems Only: Stock tanks are high hazard cross connections because of the potential for protozoan, bacterial and viral contamination. An approved air gap or atmospheric vacuum breaker or greater backflow prevention device must be installed at the tank(s). |
| mangDatPropOpN | (Management) Is the treatment plant being properly operated to prevent inadequately treated water from being sent to the distribution system? | The treatment plant is not being operated to prevent inadequately treated water from being sent to the distribution system*. During the sanitary survey the operator demonstrated lack of operational understanding or other limiting conditions existed [describe]. [Describe potential concern and remedy] |
| mangDatEmerRespPlnN | (Management) Does the system have an emergency response plan (ERP) – system does not need to show the surveyor the ERP --that includes: | No emergency response plan (ERP). The Emergency Response Plan (ERP) must detail emergency operations procedures for possible foreseeable emergencies such as power outage, loss of water, equipment failure, development of unsafe conditions, and other emergency conditions. Templates, including instructions, for developing ERPs may be found on the USEPA Region 8 Drinking Water Online website: http://www2.epa.gov/region8-waterops/reporting-forms-and-instructions-reporting-forms. Select the “Emergency Response Plan Templates” link on the main page. |
| SIGNIFICANT DEFICIENCIES | Question in Survey Form | Message |
| chkCertOpN | (Inventory) Certified Operator*? | No certified operator. Certified drinking water operators are essential to providing safe drinking water and protecting the public health of Wyoming public water systems. Regulations promulgated under the Safe Drinking Water Act require that public water systems be operated by qualified personnel. EPA Region 8 requires all community water systems and non-transient non-community water systems to have, or agree to obtain, a certified operator. To address this significant deficiency, submittal of a Wyoming certified operator certificate or other documentation will be required to demonstrate that the operator has achieved the appropriate level of certification. Alternatively, the system could employ a certified contract operator; documentation will be required to show the contractual agreement and the contract operator’s certification level. Information on certified Wyoming contract operators may be found at the following website: https://deq.state.wy.us/wqd/www/opcert/ContractOperator.aspx. |
| chkCSStdingWtrLk1 | (Consecutive Systems) Does standing water exist in any meter pits? Yes No If so, what is the source of the standing water? Leaks | Master meter vault contains standing water from leaking water system components*. (see photo #) The master meter vault at the connection to the [wholesaler] water system contained standing water caused by leaking water system components in the vault. This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. The components must be repaired to halt the leakage. |
| chkCSStdingWtrLk2 | (Consecutive Systems) Does standing water exist in any meter pits? Yes No If so, what is the source of the standing water? Leaks | Master meter vault contains standing water from leaking water system components*. (see photo #) The master meter vault at the connection to the [wholesaler] water system contained standing water caused by leaking water system components in the vault. This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. The components must be repaired to halt the leakage. |
| chkCSStdingWtrLk3 | (Consecutive Systems) Does standing water exist in any meter pits? Yes No If so, what is the source of the standing water? Leaks | Master meter vault contains standing water from leaking water system components*. (see photo #) The master meter vault at the connection to the [wholesaler] water system contained standing water caused by leaking water system components in the vault. This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. The components must be repaired to halt the leakage. |
| chkCSStdingWtrDtkn1 | (Consecutive Systems) Does standing water exist in any meter pits? Yes No If so, what is the source of the standing water? Don’t know | Master meter vault contains standing water from unknown origin*. (see photo #) The master meter vault at the connection to the [wholesaler] water system contained standing water caused by unknown source(s). This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. Since the [consecutive] is responsible for the maintenance of the master meter connection, the [consecutive] must identify the source of the standing water. If the source of the water is leakage from water system components, these must be repaired according to a schedule that you submit to the EPA. |
| chkCSStdingWtrDtkn2 | (Consecutive Systems) Does standing water exist in any meter pits? Yes No If so, what is the source of the standing water? Don’t know | Master meter vault contains standing water from unknown origin*. (see photo #) The master meter vault at the connection to the [wholesaler] water system contained standing water caused by unknown source(s). This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. Since the [consecutive] is responsible for the maintenance of the master meter connection, the [consecutive] must identify the source of the standing water. If the source of the water is leakage from water system components, these must be repaired according to a schedule that you submit to the EPA. |
| chkCSStdingWtrDtkn3 | (Consecutive Systems) Does standing water exist in any meter pits? Yes No If so, what is the source of the standing water? Don’t know | Master meter vault contains standing water from unknown origin*. (see photo #) The master meter vault at the connection to the [wholesaler] water system contained standing water caused by unknown source(s). This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. Since the [consecutive] is responsible for the maintenance of the master meter connection, the [consecutive] must identify the source of the standing water. If the source of the water is leakage from water system components, these must be repaired according to a schedule that you submit to the EPA. |
| chkTiteCapFilPortN | (Consecutive Systems) Is there a watertight cap on the (water system’s) fill port? | The water system’s fill port does not have a watertight cap. The cap on the water system’s fill port is not watertight. This could lead to the introduction of contamination into the distribution system. The cap must be repaired or replaced. |
| chk1WSStdingWtrLk | (Wholesale Systems) Does standing water exist in any meter pits for which the wholesale system is responsible? Yes No If so, what is the source of the standing water? Leaks | Master meter vault contains standing water from leaking water system components*. (see photo #) The master meter vault at the connection to the [consecutive] water system contained standing water caused by leaking water system components in the vault. This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. The components must be repaired to halt the leakage. |
| chk2WSStdingWtrLk | (Wholesale Systems) Does standing water exist in any meter pits for which the wholesale system is responsible? Yes No If so, what is the source of the standing water? Leaks | Master meter vault contains standing water from leaking water system components*. (see photo #) The master meter vault at the connection to the [consecutive] water system contained standing water caused by leaking water system components in the vault. This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. The components must be repaired to halt the leakage. |
| chk3WSStdingWtrLk | (Wholesale Systems) Does standing water exist in any meter pits for which the wholesale system is responsible? Yes No If so, what is the source of the standing water? Leaks | Master meter vault contains standing water from leaking water system components*. (see photo #) The master meter vault at the connection to the [consecutive] water system contained standing water caused by leaking water system components in the vault. This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. The components must be repaired to halt the leakage. |
| chk1WSStdingWtLkDK | (Wholesale Systems) Does standing water exist in any meter pits for which the wholesale system is responsible? Yes No If so, what is the source of the standing water? Don’t know | Master meter vault contains standing water from unknown origin*. (see photo #) The master meter vault at the connection to the [consecutive] water system contained standing water caused by unknown source(s). This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. Since the [wholesaler] is responsible for the maintenance of the master meter connection, the [wholesaler] must identify the source of the standing water. If the source of the water is leakage from water system components, these must be repaired according to a schedule that you submit to the EPA. |
| chk2WSStdingWtLkDK | (Wholesale Systems) Does standing water exist in any meter pits for which the wholesale system is responsible? Yes No If so, what is the source of the standing water? Don’t know | Master meter vault contains standing water from unknown origin*. (see photo #) The master meter vault at the connection to the [consecutive] water system contained standing water caused by unknown source(s). This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. Since the [wholesaler] is responsible for the maintenance of the master meter connection, the [wholesaler] must identify the source of the standing water. If the source of the water is leakage from water system components, these must be repaired according to a schedule that you submit to the EPA. |
| chk3WSStdingWtLkDK | (Wholesale Systems) Does standing water exist in any meter pits for which the wholesale system is responsible? Yes No If so, what is the source of the standing water? Don’t know | Master meter vault contains standing water from unknown origin*. (see photo #) The master meter vault at the connection to the [consecutive] water system contained standing water caused by unknown source(s). This water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. Since the [wholesaler] is responsible for the maintenance of the master meter connection, the [wholesaler] must identify the source of the standing water. If the source of the water is leakage from water system components, these must be repaired according to a schedule that you submit to the EPA. |
| WL1ConsInactY | (Source Data – Wells) Does system want this well to be considered inactive? | Clarify Status of Groundwater Well and Perform Appropriate Monitoring, Physical Disconnection, or Abandonment*. During the sanitary survey, the EPA was notified that this well is considered inactive and there are no plans to use it for potable water. Please note that if you wish to keep the existing well physically connected as a backup source, you must monitor this well for compliance in the same way you would if the well was used on a regular basis. This well will also be inspected as part of the sanitary survey and you must address any significant deficiencies related to this well. If you wish this well to be considered inactive, it must be either plugged and abandoned, or physically disconnected from the system. This means the line from the well to the pumphouse or to the transmission line must be severed (section of piping removed) and properly capped, or the pump must be removed, or the power source to the well pump must be physically disconnected (e.g. wires removed). The well must also be valved off to keep stagnant water from entering the system. In order to correct this significant deficiency, please confirm whether this well is active or inactive. If this well is to be considered inactive, it must be physically disconnected or abandoned. Photos must be taken to document the inactive status of this well, and should be provided to EPA with your completed correction notice. |
| WL1VehicleProtectN | (Source Data – Wells) Adequately protected from vehicle damage? | Well not adequately protected from vehicle damage. (see photo #) The wellhead must be adequately protected to prevent damage due to vehicle operations. |
| WL1PitSumpPumpN | (Source Data – Wells) If the pit or vault is not watertight, is it completed with drainage or a sump pump for permanent or portable use? | Lack of drainage for well in pit or vault*. (see photo #) When a well is in a pit or vault that is not watertight, the pit or vault shall be constructed with proper drainage or an adequate permanent or portable pump that achieves proper drainage shall be provided. Adequate drainage means that the floor of the vault must be dry at all times and only the below-grade sump can retain a small amount of water between pumping events. |
| WL1SWDrainN | (Source Data – Wells) Does SW runoff drain away from the wellhead (including wells in pits or vaults)? | Well area subject to surface drainage. (see photo #) The wellhead is located in a low-lying area where surface water may drain toward the wellhead. The area surrounding the well must be recontoured, raised and sloped to drain surface water away from the wellhead. Permanent casing for the well must remain at least 18 inches above the natural ground surface. Drainage away from the well may also be accomplished by utilizing diversionary structures such as berms, walls, or ditches. |
| WL1CasTerm12InN | (Source Data – Wells) Does well casing terminate at least 12” above the concrete floor? | Insufficient well height*. (see photo #) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above the natural ground surface. |
| WL1CasTerm18InGrdN | (Source Data – Wells) Does the well casing terminate at least 18” above the natural ground surface? | Insufficient well height*. (see photo # ) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above natural ground surface. |
| WL1HolesinWellY | (Source Data – Wells) Any holes or openings observed in the well or its appurtenances? | Holes or openings observed in the well or its appurtenances*. (see photo # ) To prevent contamination of the well, all openings must be sealed and watertight. [describe what must be sealed]. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. |
| WL1SanSealN | (Source Data – Wells) Does the well have a sanitary seal with tightly bolted cap? (No) | Lack of a sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. |
| WL1SanSealUnk | (Source Data – Wells) Does the well have a sanitary seal with tightly bolted cap? (Unknown) | Unknown integrity of sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. The surveyor was unable to determine the integrity of the seal during the survey; photo documentation must be provided showing the seal (describe what is needed such as remove the cap, etc.). |
| WL1VentAbvCasN | (Source Data – Wells) Does the vent terminate at or above the top of the casing or pitless unit? | Well vent height improvement needed*. (see photo #) The height of the well vent must be at least as high as the well casing or pitless unit. |
| WL1VentFaceDwnN | (Source Data – Wells) Is vent facing downward? | Well vent position improvement needed*. (see photo #) The vent must terminate in a downturned position. |
| WL1Screen24MeshN | (Source Data – Wells) Vent screened with #24-mesh? | Well vent screening improvement needed*. (see photo #) The well vent must be screened with a #24-mesh corrosion-resistant screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| WL1DischargPipDwnrdN | (Source Data – Wells) Discharge Piping Termination- In a downward position? | Well air release-vacuum relief valve improvement needed. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate in a downturned position. The modified piping design must also maintain at least 8 inches above the floor. |
| WL1DischrgPip8InAbN | (Source Data – Wells) Discharge Piping Termination- At least 8” above the floor? | Insufficient height of well air release-vacuum relief valve. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate at least 8 inches above the floor. The modified piping design must still terminate in a downward position. |
| WL1DischrgPip24MshN | (Source Data – Wells) Discharge Piping Termination- Screened with #24-mesh? | Screening of well air release-vacuum relief valve improvement needed. (see photo #) For well pipes equipped with an air release-vacuum relief valve, the air release piping must be covered with a #24-mesh corrosion-resistant screen. |
| WL1PumpSubjFloodY | (Source Data – Wells) Is the external pump subject to flooding? | External pump on well subject to flooding*. Flood water could create a potential backflow problem if the system loses pressure and surface water is siphoned back into the well piping. The pump should be re-located or adequately protected from flooding. |
| WL1SrWTpGWN | Well lacks Ground Water Rule sample tap.* | As required under the Ground Water Rule, a raw water sample tap must be installed so that water samples can be collected directly from the water source to determine the quality of the groundwater supply before treatment. The sample tap must be installed prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| WL1TpPriPTN | Ground Water Rule sample tap must be relocated or reconfigured.* | As required under the Ground Water Rule, the raw water sample tap must represent water collected directly from the water source to determine the quality of the groundwater supply. The sample tap for the well must be relocated so that it is prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| WL2ConsInactY | (Source Data – Wells) Does system want this well to be considered inactive? | Clarify Status of Groundwater Well and Perform Appropriate Monitoring, Physical Disconnection, or Abandonment*. During the sanitary survey, the EPA was notified that this well is considered inactive and there are no plans to use it for potable water. Please note that if you wish to keep the existing well physically connected as a backup source, you must monitor this well for compliance in the same way you would if the well was used on a regular basis. This well will also be inspected as part of the sanitary survey and you must address any significant deficiencies related to this well. If you wish this well to be considered inactive, it must be either plugged and abandoned, or physically disconnected from the system. This means the line from the well to the pumphouse or to the transmission line must be severed (section of piping removed) and properly capped, or the pump must be removed, or the power source to the well pump must be physically disconnected (e.g. wires removed). The well must also be valved off to keep stagnant water from entering the system. In order to correct this significant deficiency, please confirm whether this well is active or inactive. If this well is to be considered inactive, it must be physically disconnected or abandoned. Photos must be taken to document the inactive status of this well, and should be provided to EPA with your completed correction notice. |
| WL2VehicleProtectN | (Source Data – Wells) Adequately protected from vehicle damage? | Well not adequately protected from vehicle damage. (see photo #) The wellhead must be adequately protected to prevent damage due to vehicle operations. |
| WL2PitSumpPumpN | (Source Data – Wells) If the pit or vault is not watertight, is it completed with drainage or a sump pump for permanent or portable use? | Lack of drainage for well in pit or vault*. (see photo #) When a well is in a pit or vault that is not watertight, the pit or vault shall be constructed with proper drainage or an adequate permanent or portable pump that achieves proper drainage shall be provided. Adequate drainage means that the floor of the vault must be dry at all times and only the below-grade sump can retain a small amount of water between pumping events. |
| WL2SWDrainN | (Source Data – Wells) Does SW runoff drain away from the wellhead (including wells in pits or vaults)? | Well area subject to surface drainage. (see photo #) The wellhead is located in a low-lying area where surface water may drain toward the wellhead. The area surrounding the well must be recontoured, raised and sloped to drain surface water away from the wellhead. Permanent casing for the well must remain at least 18 inches above the natural ground surface. Drainage away from the well may also be accomplished by utilizing diversionary structures such as berms, walls, or ditches. |
| WL2CasTerm12InN | (Source Data – Wells) Does well casing terminate at least 12” above the concrete floor? | Insufficient well height*. (see photo #) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above the natural ground surface. |
| WL2CasTerm18InGrdN | (Source Data – Wells) Does the well casing terminate at least 18” above the natural ground surface? | Insufficient well height*. (see photo # ) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above natural ground surface. |
| WL2HolesinWellY | (Source Data – Wells) Any holes or openings observed in the well or its appurtenances? | Holes or openings observed in the well or its appurtenances*. (see photo # ) To prevent contamination of the well, all openings must be sealed and watertight. [describe what must be sealed]. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. |
| WL2SanSealN | (Source Data – Wells) Does the well have a sanitary seal? | Lack of a sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. |
| WL2SanSealUnk | (Source Data – Wells) Does the well have a sanitary seal with tightly bolted cap? (Unknown) | Unknown integrity of sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. The surveyor was unable to determine the integrity of the seal during the survey; photo documentation must be provided showing the seal (describe what is needed such as remove the cap, etc.). |
| WL2VentAbvCasN | (Source Data – Wells) Does the vent terminate at or above the top of the casing or pitless unit? | Well vent height improvement needed*. (see photo #) The height of the well vent must be at least as high as the well casing or pitless unit. |
| WL2VentFaceDwnN | (Source Data – Wells) Is vent facing downward? | Well vent position improvement needed*. (see photo #) The vent must terminate in a downturned position. |
| WL2Screen24MeshN | (Source Data – Wells) Vent screened with #24-mesh? | Well vent screening improvement needed*. (see photo #) The well vent must be screened with a #24-mesh corrosion-resistant screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| WL2DischargPipDwnrdN | (Source Data – Wells) Discharge Piping Termination- In a downward position? | Well air release-vacuum relief valve improvement needed. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate in a downturned position. The modified piping design must also maintain at least 8 inches above the floor. |
| WL2DischrgPip8InAbN | (Source Data – Wells) Discharge Piping Termination- At least 8” above the floor? | Insufficient height of well air release-vacuum relief valve. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate at least 8 inches above the floor. The modified piping design must still terminate in a downward position. |
| WL2DischrgPip24MshN | (Source Data – Wells) Discharge Piping Termination- Screened with #24-mesh? | Screening of well air release-vacuum relief valve improvement needed. (see photo #) For well pipes equipped with an air release-vacuum relief valve, the air release piping must be covered with a #24-mesh corrosion-resistant screen. |
| WL2PumpSubjFloodY | (Source Data – Wells) Is the external pump subject to flooding? | External pump on well subject to flooding*. Flood water could create a potential backflow problem if the system loses pressure and surface water is siphoned back into the well piping. The pump should be re-located or adequately protected from flooding. |
| WL2SrWTpGWN | Well lacks Ground Water Rule sample tap.* | As required under the Ground Water Rule, a raw water sample tap must be installed so that water samples can be collected directly from the water source to determine the quality of the groundwater supply before treatment. The sample tap must be installed prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| WL2TpPriPTN | Ground Water Rule sample tap must be relocated or reconfigured.* | As required under the Ground Water Rule, the raw water sample tap must represent water collected directly from the water source to determine the quality of the groundwater supply. The sample tap for the well must be relocated so that it is prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| WL3ConsInactY | (Source Data – Wells) Does system want this well to be considered inactive? | Clarify Status of Groundwater Well and Perform Appropriate Monitoring, Physical Disconnection, or Abandonment*. During the sanitary survey, the EPA was notified that this well is considered inactive and there are no plans to use it for potable water. Please note that if you wish to keep the existing well physically connected as a backup source, you must monitor this well for compliance in the same way you would if the well was used on a regular basis. This well will also be inspected as part of the sanitary survey and you must address any significant deficiencies related to this well. If you wish this well to be considered inactive, it must be either plugged and abandoned, or physically disconnected from the system. This means the line from the well to the pumphouse or to the transmission line must be severed (section of piping removed) and properly capped, or the pump must be removed, or the power source to the well pump must be physically disconnected (e.g. wires removed). The well must also be valved off to keep stagnant water from entering the system. In order to correct this significant deficiency, please confirm whether this well is active or inactive. If this well is to be considered inactive, it must be physically disconnected or abandoned. Photos must be taken to document the inactive status of this well, and should be provided to EPA with your completed correction notice. |
| WL3VehicleProtectN | (Source Data – Wells) Adequately protected from vehicle damage? | Well not adequately protected from vehicle damage. (see photo #) The wellhead must be adequately protected to prevent damage due to vehicle operations. |
| WL3PitSumpPumpN | (Source Data – Wells) If the pit or vault is not watertight, is it completed with drainage or a sump pump for permanent or portable use? | Lack of drainage for well in pit or vault*. (see photo #) When a well is in a pit or vault that is not watertight, the pit or vault shall be constructed with proper drainage or an adequate permanent or portable pump that achieves proper drainage shall be provided. Adequate drainage means that the floor of the vault must be dry at all times and only the below-grade sump can retain a small amount of water between pumping events. |
| WL3SWDrainN | (Source Data – Wells) Does SW runoff drain away from the wellhead (including wells in pits or vaults)? | Well area subject to surface drainage. (see photo #) The wellhead is located in a low-lying area where surface water may drain toward the wellhead. The area surrounding the well must be recontoured, raised and sloped to drain surface water away from the wellhead. Permanent casing for the well must remain at least 18 inches above the natural ground surface. Drainage away from the well may also be accomplished by utilizing diversionary structures such as berms, walls, or ditches. |
| WL3CasTerm12InN | (Source Data – Wells) Does well casing terminate at least 12” above the concrete floor? | Insufficient well height*. (see photo #) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above the natural ground surface. |
| WL3CasTerm18InGrdN | (Source Data – Wells) Does the well casing terminate at least 18” above the natural ground surface? | Insufficient well height*. (see photo # ) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above natural ground surface. |
| WL3HolesinWellY | (Source Data – Wells) Any holes or openings observed in the well or its appurtenances? | Holes or openings observed in the well or its appurtenances*. (see photo # ) To prevent contamination of the well, all openings must be sealed and watertight. [describe what must be sealed]. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. |
| WL3SanSealN | (Source Data – Wells) Does the well have a sanitary seal? | Lack of a sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. |
| WL3SanSealUnk | (Source Data – Wells) Does the well have a sanitary seal with tightly bolted cap? (Unknown) | Unknown integrity of sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. The surveyor was unable to determine the integrity of the seal during the survey; photo documentation must be provided showing the seal (describe what is needed such as remove the cap, etc.). |
| WL3VentAbvCasN | (Source Data – Wells) Does the vent terminate at or above the top of the casing or pitless unit? | Well vent height improvement needed*. (see photo #) The height of the well vent must be at least as high as the well casing or pitless unit. |
| WL3VentFaceDwnN | (Source Data – Wells) Is vent facing downward? | Well vent position improvement needed*. (see photo #) The vent must terminate in a downturned position. |
| WL3Screen24MeshN | (Source Data – Wells) Vent screened with #24-mesh? | Well vent screening improvement needed*. (see photo #) The well vent must be screened with a #24-mesh corrosion-resistant screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| WL3DischargPipDwnrdN | (Source Data – Wells) Discharge Piping Termination- In a downward position? | Well air release-vacuum relief valve improvement needed. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate in a downturned position. The modified piping design must also maintain at least 8 inches above the floor. |
| WL3DischrgPip8InAbN | (Source Data – Wells) Discharge Piping Termination- At least 8” above the floor? | Insufficient height of well air release-vacuum relief valve. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate at least 8 inches above the floor. The modified piping design must still terminate in a downward position. |
| WL3DischrgPip24MshN | (Source Data – Wells) Discharge Piping Termination- Screened with #24-mesh? | Screening of well air release-vacuum relief valve improvement needed. (see photo #) For well pipes equipped with an air release-vacuum relief valve, the air release piping must be covered with a #24-mesh corrosion-resistant screen. |
| WL3PumpSubjFloodY | (Source Data – Wells) Is the external pump subject to flooding? | External pump on well subject to flooding*. Flood water could create a potential backflow problem if the system loses pressure and surface water is siphoned back into the well piping. The pump should be re-located or adequately protected from flooding. |
| WL3SrWTpGWN | Well lacks Ground Water Rule sample tap.* | As required under the Ground Water Rule, a raw water sample tap must be installed so that water samples can be collected directly from the water source to determine the quality of the groundwater supply before treatment. The sample tap must be installed prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| WL3TpPriPTN | Ground Water Rule sample tap must be relocated or reconfigured.* | As required under the Ground Water Rule, the raw water sample tap must represent water collected directly from the water source to determine the quality of the groundwater supply. The sample tap for the well must be relocated so that it is prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| WL4ConsInactY | (Source Data – Wells) Does system want this well to be considered inactive? | Clarify Status of Groundwater Well and Perform Appropriate Monitoring, Physical Disconnection, or Abandonment*. During the sanitary survey, the EPA was notified that this well is considered inactive and there are no plans to use it for potable water. Please note that if you wish to keep the existing well physically connected as a backup source, you must monitor this well for compliance in the same way you would if the well was used on a regular basis. This well will also be inspected as part of the sanitary survey and you must address any significant deficiencies related to this well. If you wish this well to be considered inactive, it must be either plugged and abandoned, or physically disconnected from the system. This means the line from the well to the pumphouse or to the transmission line must be severed (section of piping removed) and properly capped, or the pump must be removed, or the power source to the well pump must be physically disconnected (e.g. wires removed). The well must also be valved off to keep stagnant water from entering the system. In order to correct this significant deficiency, please confirm whether this well is active or inactive. If this well is to be considered inactive, it must be physically disconnected or abandoned. Photos must be taken to document the inactive status of this well, and should be provided to EPA with your completed correction notice. |
| WL4PitSumpPumpN | (Source Data – Wells) If the pit or vault is not watertight, is it completed with drainage or a sump pump for permanent or portable use? | Lack of drainage for well in pit or vault*. (see photo #) When a well is in a pit or vault that is not watertight, the pit or vault shall be constructed with proper drainage or an adequate permanent or portable pump that achieves proper drainage shall be provided. Adequate drainage means that the floor of the vault must be dry at all times and only the below-grade sump can retain a small amount of water between pumping events. |
| WL4SWDrainN | (Source Data – Wells) Does SW runoff drain away from the wellhead (including wells in pits or vaults)? | Well area subject to surface drainage. (see photo #) The wellhead is located in a low-lying area where surface water may drain toward the wellhead. The area surrounding the well must be recontoured, raised and sloped to drain surface water away from the wellhead. Permanent casing for the well must remain at least 18 inches above the natural ground surface. Drainage away from the well may also be accomplished by utilizing diversionary structures such as berms, walls, or ditches. |
| WL4CasTerm12InN | (Source Data – Wells) Does well casing terminate at least 12” above the concrete floor? | Insufficient well height*. (see photo #) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above the natural ground surface. |
| WL4CasTerm18InGrdN | (Source Data – Wells) Does the well casing terminate at least 18” above the natural ground surface? | Insufficient well height*. (see photo # ) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above natural ground surface. |
| WL4HolesinWellY | (Source Data – Wells) Any holes or openings observed in the well or its appurtenances? | Holes or openings observed in the well or its appurtenances*. (see photo # ) To prevent contamination of the well, all openings must be sealed and watertight. [describe what must be sealed]. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. |
| WL4SanSealN | (Source Data – Wells) Does the well have a sanitary seal? | Lack of a sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. |
| WL4SanSealUnk | (Source Data – Wells) Does the well have a sanitary seal with tightly bolted cap? (Unknown) | Unknown integrity of sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. The surveyor was unable to determine the integrity of the seal during the survey; photo documentation must be provided showing the seal (describe what is needed such as remove the cap, etc.). |
| WL4VentAbvCasN | (Source Data – Wells) Does the vent terminate at or above the top of the casing or pitless unit? | Well vent height improvement needed*. (see photo #) The height of the well vent must be at least as high as the well casing or pitless unit. |
| WL4VentFaceDwnN | (Source Data – Wells) Is vent facing downward? | Well vent position improvement needed*. (see photo #) The vent must terminate in a downturned position. |
| WL4Screen24MeshN | (Source Data – Wells) Vent screened with #24-mesh? | Well vent screening improvement needed*. (see photo #) The well vent must be screened with a #24-mesh corrosion-resistant screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| WL4DischargPipDwnrdN | (Source Data – Wells) Discharge Piping Termination- In a downward position? | Well air release-vacuum relief valve improvement needed. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate in a downturned position. The modified piping design must also maintain at least 8 inches above the floor. |
| WL4DischrgPip8InAbN | (Source Data – Wells) Discharge Piping Termination- At least 8” above the floor? | Insufficient height of well air release-vacuum relief valve. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate at least 8 inches above the floor. The modified piping design must still terminate in a downward position. |
| WL4DischrgPip24MshN | (Source Data – Wells) Discharge Piping Termination- Screened with #24-mesh? | Screening of well air release-vacuum relief valve improvement needed. (see photo #) For well pipes equipped with an air release-vacuum relief valve, the air release piping must be covered with a #24-mesh corrosion-resistant screen. |
| WL4PumpSubjFloodY | (Source Data – Wells) Is the external pump subject to flooding? | External pump on well subject to flooding*. Flood water could create a potential backflow problem if the system loses pressure and surface water is siphoned back into the well piping. The pump should be re-located or adequately protected from flooding. |
| WL4SrWTpGWN | Well lacks Ground Water Rule sample tap.* | As required under the Ground Water Rule, a raw water sample tap must be installed so that water samples can be collected directly from the water source to determine the quality of the groundwater supply before treatment. The sample tap must be installed prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| WL4TpPriPTN | Ground Water Rule sample tap must be relocated or reconfigured.* | As required under the Ground Water Rule, the raw water sample tap must represent water collected directly from the water source to determine the quality of the groundwater supply. The sample tap for the well must be relocated so that it is prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| WL5ConsInactY | (Source Data – Wells) Does system want this well to be considered inactive? | Clarify Status of Groundwater Well and Perform Appropriate Monitoring, Physical Disconnection, or Abandonment*. During the sanitary survey, the EPA was notified that this well is considered inactive and there are no plans to use it for potable water. Please note that if you wish to keep the existing well physically connected as a backup source, you must monitor this well for compliance in the same way you would if the well was used on a regular basis. This well will also be inspected as part of the sanitary survey and you must address any significant deficiencies related to this well. If you wish this well to be considered inactive, it must be either plugged and abandoned, or physically disconnected from the system. This means the line from the well to the pumphouse or to the transmission line must be severed (section of piping removed) and properly capped, or the pump must be removed, or the power source to the well pump must be physically disconnected (e.g. wires removed). The well must also be valved off to keep stagnant water from entering the system. In order to correct this significant deficiency, please confirm whether this well is active or inactive. If this well is to be considered inactive, it must be physically disconnected or abandoned. Photos must be taken to document the inactive status of this well, and should be provided to EPA with your completed correction notice. |
| WL5VehicleProtectN | (Source Data – Wells) Adequately protected from vehicle damage? | Well not adequately protected from vehicle damage. (see photo #) The wellhead must be adequately protected to prevent damage due to vehicle operations. |
| WL5PitSumpPumpN | (Source Data – Wells) If the pit or vault is not watertight, is it completed with drainage or a sump pump for permanent or portable use? | Lack of drainage for well in pit or vault*. (see photo #) When a well is in a pit or vault that is not watertight, the pit or vault shall be constructed with proper drainage or an adequate permanent or portable pump that achieves proper drainage shall be provided. Adequate drainage means that the floor of the vault must be dry at all times and only the below-grade sump can retain a small amount of water between pumping events. |
| WL5SWDrainN | (Source Data – Wells) Does SW runoff drain away from the wellhead (including wells in pits or vaults)? | Well area subject to surface drainage. (see photo #) The wellhead is located in a low-lying area where surface water may drain toward the wellhead. The area surrounding the well must be recontoured, raised and sloped to drain surface water away from the wellhead. Permanent casing for the well must remain at least 18 inches above the natural ground surface. Drainage away from the well may also be accomplished by utilizing diversionary structures such as berms, walls, or ditches. |
| WL5CasTerm12InN | (Source Data – Wells) Does well casing terminate at least 12” above the concrete floor? | Insufficient well height*. (see photo #) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above the natural ground surface. |
| WL5CasTerm18InGrdN | (Source Data – Wells) Does the well casing terminate at least 18” above the natural ground surface? | Insufficient well height*. (see photo # ) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above natural ground surface. |
| WL5HolesinWellY | (Source Data – Wells) Any holes or openings observed in the well or its appurtenances? | Holes or openings observed in the well or its appurtenances*. (see photo # ) To prevent contamination of the well, all openings must be sealed and watertight. [describe what must be sealed]. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. |
| WL5SanSealN | (Source Data – Wells) Does the well have a sanitary seal? | Lack of a sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. |
| WL5SanSealUnk | (Source Data – Wells) Does the well have a sanitary seal with tightly bolted cap? (Unknown) | Unknown integrity of sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. The surveyor was unable to determine the integrity of the seal during the survey; photo documentation must be provided showing the seal (describe what is needed such as remove the cap, etc.). |
| WL5VentAbvCasN | (Source Data – Wells) Does the vent terminate at or above the top of the casing or pitless unit? | Well vent height improvement needed*. (see photo #) The height of the well vent must be at least as high as the well casing or pitless unit. |
| WL5VentFaceDwnN | (Source Data – Wells) Is vent facing downward? | Well vent position improvement needed*. (see photo #) The vent must terminate in a downturned position. |
| WL5Screen24MeshN | (Source Data – Wells) Vent screened with #24-mesh? | Well vent screening improvement needed*. (see photo #) The well vent must be screened with a #24-mesh corrosion-resistant screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| WL5DischargPipDwnrdN | (Source Data – Wells) Discharge Piping Termination- In a downward position? | Well air release-vacuum relief valve improvement needed. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate in a downturned position. The modified piping design must also maintain at least 8 inches above the floor. |
| WL5DischrgPip8InAbN | (Source Data – Wells) Discharge Piping Termination- At least 8” above the floor? | Insufficient height of well air release-vacuum relief valve. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate at least 8 inches above the floor. The modified piping design must still terminate in a downward position. |
| WL5DischrgPip24MshN | (Source Data – Wells) Discharge Piping Termination- Screened with #24-mesh? | Screening of well air release-vacuum relief valve improvement needed. (see photo #) For well pipes equipped with an air release-vacuum relief valve, the air release piping must be covered with a #24-mesh corrosion-resistant screen. |
| WL5PumpSubjFloodY | (Source Data – Wells) Is the external pump subject to flooding? | External pump on well subject to flooding*. Flood water could create a potential backflow problem if the system loses pressure and surface water is siphoned back into the well piping. The pump should be re-located or adequately protected from flooding. |
| WL5SrWTpGWN | Well lacks Ground Water Rule sample tap.* | As required under the Ground Water Rule, a raw water sample tap must be installed so that water samples can be collected directly from the water source to determine the quality of the groundwater supply before treatment. The sample tap must be installed prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| WL5TpPriPTN | Ground Water Rule sample tap must be relocated or reconfigured.* | As required under the Ground Water Rule, the raw water sample tap must represent water collected directly from the water source to determine the quality of the groundwater supply. The sample tap for the well must be relocated so that it is prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| WL6ConsInactY | (Source Data – Wells) Does system want this well to be considered inactive? | Clarify Status of Groundwater Well and Perform Appropriate Monitoring, Physical Disconnection, or Abandonment*. During the sanitary survey, the EPA was notified that this well is considered inactive and there are no plans to use it for potable water. Please note that if you wish to keep the existing well physically connected as a backup source, you must monitor this well for compliance in the same way you would if the well was used on a regular basis. This well will also be inspected as part of the sanitary survey and you must address any significant deficiencies related to this well. If you wish this well to be considered inactive, it must be either plugged and abandoned, or physically disconnected from the system. This means the line from the well to the pumphouse or to the transmission line must be severed (section of piping removed) and properly capped, or the pump must be removed, or the power source to the well pump must be physically disconnected (e.g. wires removed). The well must also be valved off to keep stagnant water from entering the system. In order to correct this significant deficiency, please confirm whether this well is active or inactive. If this well is to be considered inactive, it must be physically disconnected or abandoned. Photos must be taken to document the inactive status of this well, and should be provided to EPA with your completed correction notice. |
| WL6VehicleProtectN | (Source Data – Wells) Adequately protected from vehicle damage? | Well not adequately protected from vehicle damage. (see photo #) The wellhead must be adequately protected to prevent damage due to vehicle operations. |
| WL6PitSumpPumpN | (Source Data – Wells) If the pit or vault is not watertight, is it completed with drainage or a sump pump for permanent or portable use? | Lack of drainage for well in pit or vault*. (see photo #) When a well is in a pit or vault that is not watertight, the pit or vault shall be constructed with proper drainage or an adequate permanent or portable pump that achieves proper drainage shall be provided. Adequate drainage means that the floor of the vault must be dry at all times and only the below-grade sump can retain a small amount of water between pumping events. |
| WL6SWDrainN | (Source Data – Wells) Does SW runoff drain away from the wellhead (including wells in pits or vaults)? | Well area subject to surface drainage. (see photo #) The wellhead is located in a low-lying area where surface water may drain toward the wellhead. The area surrounding the well must be recontoured, raised and sloped to drain surface water away from the wellhead. Permanent casing for the well must remain at least 18 inches above the natural ground surface. Drainage away from the well may also be accomplished by utilizing diversionary structures such as berms, walls, or ditches. |
| WL6CasTerm12InN | (Source Data – Wells) Does well casing terminate at least 12” above the concrete floor? | Insufficient well height*. (see photo #) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above the natural ground surface. |
| WL6CasTerm18InGrdN | (Source Data – Wells) Does the well casing terminate at least 18” above the natural ground surface? | Insufficient well height*. (see photo # ) Permanent casing for all wells must project at least 12 inches above the concrete floor or apron and at least 18 inches above natural ground surface. |
| WL6HolesinWellY | (Source Data – Wells) Any holes or openings observed in the well or its appurtenances? | Holes or openings observed in the well or its appurtenances*. (see photo # ) To prevent contamination of the well, all openings must be sealed and watertight. [describe what must be sealed]. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. |
| WL6SanSealN | (Source Data – Wells) Does the well have a sanitary seal? | Lack of a sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. |
| WL6SanSealUnk | (Source Data – Wells) Does the well have a sanitary seal with tightly bolted cap? (Unknown) | Unknown integrity of sanitary seal on the well casing. (see photo #) To prevent contamination, the well must be fitted with a functioning sanitary seal and a tightly bolted cap. Caulking/sealer, due to the possibility of the inclusion of BTEX components, must not be used. The sanitary seal must be a properly fitted neoprene gasket. The surveyor was unable to determine the integrity of the seal during the survey; photo documentation must be provided showing the seal (describe what is needed such as remove the cap, etc.). |
| WL6VentAbvCasN | (Source Data – Wells) Does the vent terminate at or above the top of the casing or pitless unit? | Well vent height improvement needed*. (see photo #) The height of the well vent must be at least as high as the well casing or pitless unit. |
| WL6VentFaceDwnN | (Source Data – Wells) Is vent facing downward? | Well vent position improvement needed*. (see photo #) The vent must terminate in a downturned position. |
| WL6Screen24MeshN | (Source Data – Wells) Vent screened with #24-mesh? | Well vent screening improvement needed*. (see photo #) The well vent must be screened with a #24-mesh corrosion-resistant screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| WL6DischargPipDwnrdN | (Source Data – Wells) Discharge Piping Termination- In a downward position? | Well air release-vacuum relief valve improvement needed. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate in a downturned position. The modified piping design must also maintain at least 8 inches above the floor. |
| WL6DischrgPip8InAbN | (Source Data – Wells) Discharge Piping Termination- At least 8” above the floor? | Insufficient height of well air release-vacuum relief valve. (see photo #) For wells equipped with an air release-vacuum relief valve, the air release piping must terminate at least 8 inches above the floor. The modified piping design must still terminate in a downward position. |
| WL6DischrgPip24MshN | (Source Data – Wells) Discharge Piping Termination- Screened with #24-mesh? | Screening of well air release-vacuum relief valve improvement needed. (see photo #) For well pipes equipped with an air release-vacuum relief valve, the air release piping must be covered with a #24-mesh corrosion-resistant screen. |
| WL6PumpSubjFloodY | (Source Data – Wells) Is the external pump subject to flooding? | External pump on well subject to flooding*. Flood water could create a potential backflow problem if the system loses pressure and surface water is siphoned back into the well piping. The pump should be re-located or adequately protected from flooding. |
| WL6SrWTpGWN | Well lacks Ground Water Rule sample tap.* | As required under the Ground Water Rule, a raw water sample tap must be installed so that water samples can be collected directly from the water source to determine the quality of the groundwater supply before treatment. The sample tap must be installed prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| WL6TpPriPTN | Ground Water Rule sample tap must be relocated or reconfigured.* | As required under the Ground Water Rule, the raw water sample tap must represent water collected directly from the water source to determine the quality of the groundwater supply. The sample tap for the well must be relocated so that it is prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| sourceOPolutnNrWlY | (Source Data – Wells) Are there any sources of pollution near the wells which could impact water quality? | Source of possible contamination in immediate area of well. (see photo # ) In the vicinity of the well there is [describe sources of pollution] that can potentially impact the water quality. (Describe remedy) |
| srce456OPolutnNrWlY | (Source Data – Wells) Are there any sources of pollution near the wells which could impact water quality? | Source of possible contamination in immediate area of well. (see photo # ) In the vicinity of the well there is [describe sources of pollution] that can potentially impact the water quality. (Describe remedy) |
| WLone2or3animdropY | (Source Data – Wells) Mice or other animals and their droppings in immediate area? | Mice or other animals and their droppings in immediate area of the well (in well house, vault, or pit). (see photo # ) The mice or other animals and their droppings must be removed. Please refer to the Center for Disease Control (CDC) website regarding how to properly clean up this area to prevent contracting the Hantavirus pulmonary syndrome: http://www.cdc.gov/ncidod/diseases/hanta/hps/noframes/prevent3.htm |
| WLfour5or6animdropY | (Source Data – Wells) Mice or other animals and their droppings in immediate area? | Mice or other animals and their droppings in immediate area of the well (in well house, vault, or pit). (see photo # ) The mice or other animals and their droppings must be removed. Please refer to the Center for Disease Control (CDC) website regarding how to properly clean up this area to prevent contracting the Hantavirus pulmonary syndrome: http://www.cdc.gov/ncidod/diseases/hanta/hps/noframes/prevent3.htm |
| SprSrcFencedN | (Source Data Springs) Are the spring collection area and spring box fenced to keep animals away? | Spring collection area and collection chamber/box not fenced to keep large animals away. (see photo #) The spring collection area and collection chamber/box must be enclosed by a fence to prevent stock and large wildlife from entering the spring area. |
| properShoeBxLidN | (Source Data Springs) Proper shoe box lid? | Spring collection chamber hatch/entry improvement needed*. (see photo #) The cover must overlap the framed opening and extend down around the frame at least two inches. |
| RubberGasketOnLidN | (Source Data Springs) Rubber gasket on the lid? | Spring hatch/entry improvement needed*. (see photo # ) Spring hatches must be fitted with a solid, watertight cover with a rubber gasket. |
| AdequateAirVnt24MN | (Source Data Springs) Air vents screened with #24-mesh? | Spring air vent improvement needed*. (see photo #) The air vent must be screened with a #24-mesh corrosion-resistant screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| SprgHatchLockedN | (Source Data Springs) Is the hatch locked? | Spring hatch/entry not locked. (see photo #) Spring hatch covers must have a locking device. |
| spgScreenedOverFN | (Source Data Springs) Overflow screened with #24-mesh screen? | Spring collection chamber overflow screening improvement needed*. (see photo #) The overflow pipe must have a #24-mesh screen on the exterior discharge ends to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The modified overflow design must also still freefall at least 12 inches above ground. |
| SprOvrflFreeFall12N | (Source Data Springs) Does overflow have a free fall of at least 12 inches? | Spring collection chamber overflow improvement needed*. (see photo #) The overflow pipe must freefall at least 12 inches above ground. The modified overflow must also maintain a #24-mesh screen on the exterior discharge end. |
| sprCollChmbrWtrTiteN | (Source Data Springs) Is the spring collection chamber watertight to prevent inflow of unwanted surface water? | Spring collection chamber not watertight*. (see photo #) The chamber must be watertight to prevent inflow of unwanted surface water. |
| srcPmpSubjToFloodY | (Source Data Springs) Is the pump station subject to flooding? | External pump on spring subject to flooding*. Flood water could create a potential backflow problem if the system loses pressure and surface water is siphoned back into the spring transmission line. The pump should be re-located or adequately protected from flooding. |
| sprPropShoeBxLidN | (Source Data Springs) (Spring collection or distribution system hatches / manholes) Proper shoe box lid? | Spring collection or transmission system hatch/entry improvement needed*. (see photo #) The cover must overlap the framed opening and extend down around the frame at least two inches. [identify location of hatch in collection or transmission system] |
| sprRubbGaskLidN | (Source Data Springs) (Spring collection or distribution system hatches / manholes) Rubber gasket on the lid? | Spring collection or transmission system hatch/entry improvement needed*. (see photo #) Hatches / manholes in the spring collection and transmission system must be fitted with a solid, watertight cover with a rubber gasket. |
| sprSecureAccEntrN | (Source Data Springs) (Spring collection or distribution system hatches / manholes) Locked? | Spring collection or transmission system hatch/entry not locked. (see photo #) Hatch covers / manholes in the spring collection or transmission system must have a locking device. |
| sprSrcOfPolluNrSprY | (Source Data Springs) Are there any sources of pollution near the spring which could impact water quality? | Source of possible contamination in immediate area of spring. (see photo # ) In the vicinity of the spring there is [describe sources of pollution] that can potentially impact the water quality. [describe remedy] |
| sprSrcanimdropY | (Source Data Springs) Mice or other animals and their droppings in immediate area? | Mice or other animals and their droppings in immediate area of the spring (in spring house or collection box). (see photo # ) The mice or other animals and their droppings must be removed. Please refer to the Center for Disease Control (CDC) website regarding how to properly clean up this area to prevent contracting the Hantavirus pulmonary syndrome: http://www.cdc.gov/ncidod/diseases/hanta/hps/noframes/prevent3.htm. |
| sprSrcWTpGWN | Spring lacks Ground Water Rule sample tap.* | As required under the Ground Water Rule, a raw water sample tap must be installed so that water samples can be collected directly from the water source to determine the quality of the groundwater supply. The sample tap must be installed prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| sprTpPriPTN | Ground Water Rule sample tap must be relocated or reconfigured.* | As required under the Ground Water Rule, the raw water sample tap must represent water collected directly from the water source to determine the quality of the groundwater supply. The sample tap for the spring must be relocated so that it is prior to the water entering any treatment process or storage tank. The tap should be of the smooth-nosed type without interior or exterior threads, suitable for obtaining samples for bacteriological analysis, and should not have a screen, aerator, or other such appurtenance. |
| inflGllSourcePolluY | (Source Data Infiltration Galleries) Are there any sources of pollution near the infiltration gallery (e.g., agriculture/industrial activities, cleaning supplies, oil/fuel, etc.) which could impact water quality? | Source of possible contamination in immediate area of infiltration gallery. (see photo # ) In the vicinity of the infiltration gallery there is [describe sources of pollution] that can potentially impact the water quality. [describe remedy] |
| intStrmSrcePolluY | (Source Data Streams) Are there any sources of pollution near the stream (e.g., agriculture/industrial activities, cleaning supplies, oil/fuel, etc.) which could impact water quality? | Source of possible contamination in immediate area of stream. (see photo # ) In the vicinity of the stream there is [describe sources of pollution] that can potentially impact the water quality. [describe remedy] |
| intResvSrceSubPolluY | (Source Data Reservoirs) Are there any sources of pollution near the reservoirs, lakes and ponds and associated pumps (e.g., agriculture/industrial activities, cleaning supplies, oil/fuel, etc.) which could impact water quality? | Source of possible contamination in immediate area of reservoir. (see photo # ) In the vicinity of the reservoir there is [describe sources of pollution] that can potentially impact the water quality. [describe remedy] |
| EmergSrceSubPolluY | (Source Data Emergency Back-up Sources) Are there any sources of pollution near the emergency backup source (e.g., agriculture/industrial activities, cleaning supplies, oil/fuel, etc.) which could impact water quality? | Source of possible contamination in immediate area of emergency backup source. (see photo # ) In the vicinity of the emergency backup source there is [describe sources of pollution] that can potentially impact the water quality. [describe remedy] |
| RawTrans1ServConnY | (Raw Water Transmission) Are there any service connections to the raw water transmission line? | Customers connected to raw water transmission line*. Some customers are connected to the raw water transmission line to the treatment plant and are receiving untreated water. Delivery of non-potable water for human consumption is a public health risk. The service must be disconnected or appropriate treatment must be provided prior to use. [put site specific info about treating the water or disconnecting] |
| RawTrans2ServConnY | (Raw Water Transmission) Are there any service connections to the raw water transmission line? | Customers connected to raw water transmission line*. Some customers are connected to the raw water transmission line to the treatment plant and are receiving untreated water. Delivery of non-potable water for human consumption is a public health risk. The service must be disconnected or appropriate treatment must be provided prior to use. [put site specific info about treating the water or disconnecting] |
| distBstPSubjFldY1 | (Distribution Booster Pumps) Is the pump station subject to flooding? | Booster pump station subject to flooding [location of pump station]*. Flood water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. The pump must be re-located or adequately protected from flooding. |
| distBstPSubjFldY2 | (Distribution Booster Pumps) Is the pump station subject to flooding? | Booster pump station subject to flooding [location of pump station]*. Flood water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. The pump must be re-located or adequately protected from flooding. |
| distBstPSubjFldY3 | (Distribution Booster Pumps) Is the pump station subject to flooding? | Booster pump station subject to flooding [location of pump station]*. Flood water could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. The pump must be re-located or adequately protected from flooding. |
| hydrTnkRustY | (Hydropneumatic Tanks) Is there evidence of severe rust? | Hydropneumatic tank has evidence of severe rust*. (see photo # ) Failure to maintain the structural and sanitary integrity of the tank could lead directly to contamination within the tank, illness and/or the loss of property. The rust on the tank must be repaired or the tank must be replaced. |
| hydrTnkLeakY | (Hydropneumatic Tanks) Is there evidence of water leaks? | Hydropneumatic tank has evidence of water leaks*. (see photo # ) Failure to maintain the structural and sanitary integrity of the tank could lead directly to contamination within the tank, illness and/or the loss of property. The leaks in the tank must be repaired or the tank must be replaced. |
| hydrTnkAirLeakY | (Hydropneumatic Tanks) Is there evidence of air leaks? | Hydropneumatic tank has evidence of air leaks*. (see photo # ) Failure to maintain the structural and sanitary integrity of the tank could lead directly to contamination within the tank, illness and/or the loss of property. The leaks in the tank must be repaired or the tank must be replaced. |
| hydrTnkFloodingY | (Hydropneumatic Tanks) Is there evidence of flooding (if in a vault)? | Hydropneumatic tank in a vault with evidence of flooding*. (see photo # ) Standing water creates an environment that could damage the structural and sanitary integrity of the tank. The hydropneumatic tank must be re-located or adequately protected from standing water. |
| hydrTnkComprAgeY | (Hydropneumatic Tanks) For any tank that uses an air compressor, is the tank age older than the life expectancy? | Pressure tank that uses an air compressor is older than the manufacturer’s life expectancy*. (see photo # ) In order to protect the structural integrity of the pressure tank (prevent tank explosion), tanks that exceed manufacturer’s life expectancy must be replaced. |
| gvTk1FloodingY | (Gravity Tanks) Is the site subject to flooding? | Storage tank located in an area subject to flooding. (see photo # ) [insert site specific problem and remedy] |
| gvTk1PropMaintN | (Gravity Tanks) Does the tank appear structurally sound? | Storage tank not structurally sound or properly maintained*. (see photo # ) The storage tank does not appear to be structurally sound. Specifically, the [tank component] of the tank must be evaluated by a professional engineer familiar with the construction of water-storage tanks to determine the integrity of the tank’s [tank component]. Failure to maintain the structural and sanitary integrity of the tank could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank must be made as soon as possible and it must be repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk1FounStrucSoundN | (Gravity Tanks) Does the foundation appear structurally sound? | Storage tank foundation does not appear to be structurally sound*. (see photo # ) The storage tank foundation does not appear to be structurally sound. It must be evaluated by a professional engineer familiar with the construction of water-storage tanks. Failure to maintain the structural and sanitary integrity of the tank foundation could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank foundation must be made as soon as possible and the foundation repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk1OpeningsY | (Gravity Tanks) Are there any unprotected openings in the tank (breaches, leaks, etc)? | Storage tank not sealed*. (see photo #) Other than the openings afforded by the #24-mesh screens on the vents and overflows, all openings must be sealed completely to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. [Describe specific openings such as: All openings between the roof and sidewalls must be sealed and watertight. Any openings from antennas, telemetry, and other appurtenances must be sealed and watertight.] |
| gvTk1InspectedN | (Gravity Tanks) If the tank is more than 10 years old, was it cleaned and inspected within the last 10 years? | Storage tank not cleaned and inspected within the last 10 years. The tank must be cleaned and inspected. Please see the enclosed Finished Water Storage Tank Inspection/Cleaning Checklist for a list of items that must be evaluated during the inspection. Tanks need to be periodically cleaned and inspected to prevent the growth of potentially harmful pathogens in the accumulated sediments and to address construction issues before they require major repairs. Inspections and cleaning may be done by a third-party professional or appropriately trained in-house staff. Please be aware that some tanks may be considered as confined spaces or hazardous environments; personnel working in or near the tanks should have all OSHA-required training, and proper safety equipment and procedures should be used at all times. After inspection and cleaning the tank must be disinfected according to AWWA standards (C652-92: Disinfection of Water Storage Facilities). In order to correct this significant deficiency, you must provide EPA with the following documentation: A completed copy of the Finished Water Storage Tank Inspection/Cleaning Checklist. A copy of inspection results and labeled photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk1OvFlSepN | (Gravity Tanks) Does the tank have an overflow separate from the vent? @ | No overflow on finished water storage tank*. In order to protect the integrity of the tank in the case of control system failure leading to overfilling, the tank must have an overflow that is separate from the vent. |
| gvTk1OvFlAccessN | (Gravity Tanks) Is the overflow accessible for inspection? | Unknown integrity of storage tank overflow [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank overflow [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk1OvFl24MeshN | (Gravity Tanks) Overflow has a #24-mesh screen OR a duckbill valve OR a properly sealed flapper valve with screen inside (the EPA recommends a #24-mesh screen)? | Overflow screening on finished water storage tank improvement needed*. (see photo #) Overflows must be fitted with non-corrodible #24-mesh screen, or a properly sealed flapper or duckbill valve to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the pipe at a location least susceptible to vandalism. When a flapper valve is used, a screen must be placed inside the valve (the EPA Region 8 recommends non-corrodible #24-mesh screen be used). In cold climates, use of a flapper or duckbill valve should be considered to minimize air movement and hence ice formation in the tank. In cold climates, provisions should be considered to prevent the flapper or duckbill from freezing shut. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk1OvFlTerm12InN | (Gravity Tanks) Does the overflow line terminate no less than 12 inches but no more than 24 inches above the ground surface? | Overflow on finished water storage tank discharges at improper height*. (see photo #) Overflow must be piped to an elevation between 12 and 24 inches above the ground surface and discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk1OvDrainStructN | (Gravity Tanks) Does the overflow discharge over an inlet structure, splash plate, or engineered rip-rap? | Overflow discharge point on finished water storage tank improvement needed*. (see photo #) Overflow must discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk1OvFlConnSewerN | (Gravity Tanks) Does the overflow have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Overflow on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain*. (see photo #) No overflow may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the overflow pipe terminates at least three pipe diameters above the ground level at the sewer or storm drain, or over a splash pad. |
| gvTk1DLAccessblN | (Gravity Tanks) Is the drain accessible for inspection? | Unknown integrity of storage tank drain [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank drain [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk1DLAirGapN | (Gravity Tanks) Does the drain pipe have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Drain on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain*. (see photo #) No drain may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the drain pipe terminates at least three pipe diameters above the ground level at the sewer drain, storm drain, splash pad or engineered rip-rap. |
| gvTk1VentSepN | (Gravity Tanks) Does the tank have a vent separate from the overflow? | No vent on finished water storage tank*. In order to protect the structural integrity of the tank during changes to tank water levels, and other events affecting the confined air space, the tank must have a vent that is separate from the overflow. |
| gvTk1AirVentAccessN | (Gravity Tanks) Is the vent accessible for inspection? | Unknown integrity of storage tank air vent [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank air vent [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk1AirVntMeshN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Is there #24-mesh screen? | Air vent screening on finished water storage tank needs improvement*. (see photo #) The vent must be fitted with non-corrodible #24-mesh screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. Prior to installing the screen, the PWS should evaluate whether the tank needs a vacuum/pressure relief valve or another mechanism to prevent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk1AirVnt24AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Downturned vent: Is the vent at least 24“ above the roof? | Downturned air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24” above the tank surface to prevent inhalation of contaminants by the tank. |
| gvTk1AirVentSoldCovN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is there a solid cover down to the bottom of the vent screen? | Air vent on finished water storage tank does not have a solid cover*. (see photo #) For non-downturned vents, the screen must have a solid cover down to the bottom of the vent screen to prevent rain and snow, and minimize dust and sunlight, from entering the tank. If the cover is installed in a manner that restricts the size of the vent opening it may result in insufficient airflow and subsequent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require evaluation by a licensed engineer to ensure that no damage will occur to the existing water tank as a result of the modifications. For elevated tanks and standpipes, the EPA strongly recommends that the system install a vent with an automatic re-setting vacuum/pressure relief mechanism if one is not already in place. |
| gvTk1AirVnt8AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is the screen at least 8” above the roof surface? | Air vent on finished water storage tank is not elevated above the roof at the required height*. (see photo #) For non-downturned vents, the bottom of the vent screen must be at least 8” above the tank roof to prevent inhalation of contaminants by the tank. |
| gvTk1AirVen24MeshN | (Gravity Tanks) Below Ground (buried or partially buried) Is air vent covered with #24-mesh screen? | Air vent screening on finished water storage tank improvement needed*. (see photo #) The vent must be fitted with non-corrodible #24-mesh screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk1AirVnTermDwnN | (Gravity Tanks) Below Ground (buried or partially buried) Does the air vent terminate downward? | Air vent on finished water storage tank does not terminate in a downturned position*. (see photo #) On buried or partially buried tanks the air vent must terminate in a downturned position. |
| gvTk1AirVnTrmAbvRfN | (Gravity Tanks) Below Ground (buried or partially buried) Is the air vent at least 24” above the roof or ground surface (whichever is higher)? | Air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24 inches above the roof or ground surface (whichever is higher) to prevent rain from entering and to prevent inhalation of contaminants by the tank. |
| gvTk1AHAccessableN | (Gravity Tanks) Is the hatch accessible for inspection? | Unknown integrity of storage tank access hatch [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank access hatch [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk1bgAH24AboveRfN | (Gravity Tanks) For below ground tanks where the roof is completely buried, is the hatch raised at least 24” above ground level? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the ground surface. |
| gvTk1pbAH24AboveRfN | (Gravity Tanks) For partially buried tanks where the roof is visible, is the hatch raised at least 24” above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the surface of the roof. |
| gvTk1agAH4AboveRfN | (Gravity Tanks) For above ground tanks (ground level or elevated/standpipe): Is the hatch raised 4“ above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be framed at least four inches above the surface of the roof. |
| gvTk1AHShoeBxLidN | (Gravity Tanks) Does the hatch have a shoe box lid? | Hatch on Finished Water Storage Tank does not have a shoe box lid*. (see photo #) The tank hatch must be fitted with a solid watertight cover which extends down around the frame at least two inches. |
| gvTk1AHRubberGaskN | (Gravity Tanks) Is the lid tight and sealed with a rubber gasket? | Hatch on Finished Water Storage Tank does not have a gasket that creates a watertight seal. (see photo #) The tank hatch must have a rubber gasket to seal the hatch lid to the frame tightly to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| gvTk1AHALockedN | (Gravity Tanks) Is the hatch locked? | Hatch on Finished Water Storage Tank does not have a locking device. (see photo #) The cover must have a locking device. |
| gvTk2FloodingY | (Gravity Tanks) Is the site subject to flooding? | Storage tank located in an area subject to flooding. (see photo # ) [insert site specific problem and remedy] |
| gvTk2PropMaintN | (Gravity Tanks) Does the tank appear structurally sound? | Storage tank not structurally sound or properly maintained*. (see photo # ) The storage tank does not appear to be structurally sound. Specifically, the [tank component] of the tank must be evaluated by a professional engineer familiar with the construction of water-storage tanks to determine the integrity of the tank’s [tank component]. Failure to maintain the structural and sanitary integrity of the tank could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank must be made as soon as possible and it must be repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk2FounStrucSoundN | (Gravity Tanks) Does the foundation appear structurally sound? | Storage tank foundation does not appear to be structurally sound*. (see photo # ) The storage tank foundation does not appear to be structurally sound. It must be evaluated by a professional engineer familiar with the construction of water-storage tanks. Failure to maintain the structural and sanitary integrity of the tank foundation could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank foundation must be made as soon as possible and the foundation repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk2OpeningsY | (Gravity Tanks) Are there any unprotected openings in the tank (breaches, leaks, etc)? | Storage tank not sealed*. (see photo #) Other than the openings afforded by the #24-mesh screens on the vents and overflows, all openings must be sealed completely to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. [Describe specific openings such as: All openings between the roof and sidewalls must be sealed and watertight. Any openings from antennas, telemetry, and other appurtenances must be sealed and watertight.] |
| gvTk2InspectedN | (Gravity Tanks) If the tank is more than 10 years old, was it cleaned and inspected within the last 10 years? | Storage tank not cleaned and inspected within the last 10 years. The tank must be cleaned and inspected. Please see the enclosed Finished Water Storage Tank Inspection/Cleaning Checklist for a list of items that must be evaluated during the inspection. Tanks need to be periodically cleaned and inspected to prevent the growth of potentially harmful pathogens in the accumulated sediments and to address construction issues before they require major repairs. Inspections and cleaning may be done by a third-party professional or appropriately trained in-house staff. Please be aware that some tanks may be considered as confined spaces or hazardous environments; personnel working in or near the tanks should have all OSHA-required training, and proper safety equipment and procedures should be used at all times. After inspection and cleaning the tank must be disinfected according to AWWA standards (C652-92: Disinfection of Water Storage Facilities). In order to correct this significant deficiency, you must provide EPA with the following documentation: A completed copy of the Finished Water Storage Tank Inspection/Cleaning Checklist. A copy of inspection results and labeled photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk2OvFlSepN | (Gravity Tanks) Does the tank have an overflow separate from the vent? @ | No overflow on finished water storage tank*. In order to protect the integrity of the tank in the case of control system failure leading to overfilling, the tank must have an overflow that is separate from the vent. |
| gvTk2OvFlAccessN | (Gravity Tanks) Is the overflow accessible for inspection? | Unknown integrity of storage tank overflow [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank overflow [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk2OvFl24MeshN | (Gravity Tanks) Overflow has a #24-mesh screen OR a duckbill valve OR a properly sealed flapper valve with screen inside (the EPA recommends a #24-mesh screen)? | Overflow screening on finished water storage tank improvement needed*. (see photo #) Overflows must be fitted with non-corrodible #24-mesh screen, or a properly sealed flapper or duckbill valve to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the pipe at a location least susceptible to vandalism. When a flapper valve is used, a screen must be placed inside the valve (EPA Region 8 recommends non-corrodible #24-mesh screen be used). In cold climates, use of a flapper or duckbill valve should be considered to minimize air movement and hence ice formation in the tank. In cold climates, provisions should be considered to prevent the flapper or duckbill from freezing shut. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk2OvFlTerm12InN | (Gravity Tanks) Does the overflow line terminate no less than 12 inches but no more than 24 inches above the ground surface? | Overflow on finished water storage tank discharges at improper height*. (see photo #) Overflow must be piped to an elevation between 12 and 24 inches above the ground surface and discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk2OvDrainStructN | (Gravity Tanks) Does the overflow discharge over an inlet structure, splash plate, or engineered rip-rap? | Overflow discharge point on finished water storage tank improvement needed*. (see photo #) Overflow must discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk2OvFlConnSewerN | (Gravity Tanks) Does the overflow have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Overflow on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain. (see photo #) No overflow may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the overflow pipe terminates at least three pipe diameters above the ground level at the sewer or storm drain, or over a splash pad. |
| gvTk2DLAccessblN | (Gravity Tanks) Is the drain accessible for inspection? | Unknown integrity of storage tank drain [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank drain [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk2DLAirGapN | (Gravity Tanks) Does the drain pipe have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Drain on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain*. (see photo #) No drain may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the drain pipe terminates at least three pipe diameters above the ground level at the sewer drain, storm drain, splash pad or engineered rip-rap. |
| gvTk2VentSepN | (Gravity Tanks) Does the tank have a vent separate from the overflow? | No vent on finished water storage tank*. In order to protect the structural integrity of the tank during changes to tank water levels, and other events affecting the confined air space, the tank must have a vent that is separate from the overflow. |
| gvTk2AirVentAccessN | (Gravity Tanks) Is the vent accessible for inspection? | Unknown integrity of storage tank air vent [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank air vent [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. The EPA will review the inspection report and may require additional corrective actions. |
| gvTk2AirVntMeshN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Is there #24-mesh screen? | Air vent screening on finished water storage tank needs improvement*. (see photo #) The vent must be fitted with non-corrodible #24-mesh screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. Prior to installing the screen, the PWS should evaluate whether the tank needs a vacuum/pressure relief valve or another mechanism to prevent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk2AirVnt24AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Downturned vent: Is the vent at least 24“ above the roof? | Downturned air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24” above the tank surface to prevent inhalation of contaminants by the tank. |
| gvTk2AirVentSoldCovN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is there a solid cover down to the bottom of the vent screen? | Air vent on finished water storage tank does not have a solid cover*. (see photo #) For non-downturned vents, the screen must have a solid cover down to the bottom of the vent screen to prevent rain and snow, and minimize dust and sunlight, from entering the tank. If the cover is installed in a manner that restricts the size of the vent opening it may result in insufficient airflow and subsequent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require evaluation by a licensed engineer to ensure that no damage will occur to the existing water tank as a result of the modifications. For elevated tanks and standpipes, the EPA strongly recommends that the system install a vent with an automatic re-setting vacuum/pressure relief mechanism if one is not already in place. |
| gvTk2AirVnt8AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is the screen at least 8” above the roof surface? | Air vent on finished water storage tank is not elevated above the roof at the required height*. (see photo #) For non-downturned vents, the bottom of the vent screen must be at least 8” above the tank roof to prevent inhalation of contaminants by the tank. |
| gvTk2AirVen24MeshN | (Gravity Tanks) Below Ground (buried or partially buried) Is air vent covered with #24-mesh screen? | Air vent screening on finished water storage tank improvement needed*. (see photo #) The vent must be fitted with non-corrodible #24-mesh screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk2AirVnTermDwnN | (Gravity Tanks) Below Ground (buried or partially buried) Does the air vent terminate downward? | Air vent on finished water storage tank does not terminate in a downturned position*. (see photo #) On buried or partially buried tanks the air vent must terminate in a downturned position. |
| gvTk2AirVnTrmAbvRfN | (Gravity Tanks) Below Ground (buried or partially buried) Is the air vent at least 24” above the roof or ground surface (whichever is higher)? | Air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24 inches above the roof or ground surface (whichever is higher) to prevent rain from entering and to prevent inhalation of contaminants by the tank. |
| gvTk2AHAccessableN | (Gravity Tanks) Is the hatch accessible for inspection? | Unknown integrity of storage tank access hatch [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank access hatch [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. The EPA will review the inspection report and may require additional corrective actions. |
| gvTk2bgAH24AboveRfN | (Gravity Tanks) For below ground tanks where the roof is completely buried, is the hatch raised at least 24” above ground level? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the ground surface. |
| gvTk2pbAH24AboveRfN | (Gravity Tanks) For partially buried tanks where the roof is visible, is the hatch raised at least 24” above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the surface of the roof. |
| gvTk2agAH4AboveRfN | (Gravity Tanks) For above ground tanks (ground level or elevated/standpipe): Is the hatch raised 4“ above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be framed at least four inches above the surface of the roof. |
| gvTk2AHShoeBxLidN | (Gravity Tanks) Does the hatch have a shoe box lid? | Hatch on Finished Water Storage Tank does not have a shoe box lid*. (see photo #) The tank hatch must be fitted with a solid watertight cover which extends down around the frame at least two inches. |
| gvTk2AHRubberGaskN | (Gravity Tanks) Is the lid tight and sealed with a rubber gasket? | Hatch on Finished Water Storage Tank does not have a gasket that creates a watertight seal. (see photo #) The tank hatch must have a rubber gasket to seal the hatch lid to the frame tightly to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| gvTk2AHALockedN | (Gravity Tanks) Is the hatch locked? | Hatch on Finished Water Storage Tank does not have a locking device. (see photo #) The cover must have a locking device. |
| gvTk3FloodingY | (Gravity Tanks) Is the site subject to flooding? | Storage tank located in an area subject to flooding. (see photo # ) [insert site specific problem and remedy] |
| gvTk3PropMaintN | (Gravity Tanks) Does the tank appear structurally sound? | Storage tank not structurally sound or properly maintained*. (see photo # ) The storage tank does not appear to be structurally sound. Specifically, the [tank component] of the tank must be evaluated by a professional engineer familiar with the construction of water-storage tanks to determine the integrity of the tank’s [tank component]. Failure to maintain the structural and sanitary integrity of the tank could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank must be made as soon as possible and it must be repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk3FounStrucSoundN | (Gravity Tanks) Does the foundation appear structurally sound? | Storage tank foundation does not appear to be structurally sound*. (see photo # ) The storage tank foundation does not appear to be structurally sound. It must be evaluated by a professional engineer familiar with the construction of water-storage tanks. Failure to maintain the structural and sanitary integrity of the tank foundation could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank foundation must be made as soon as possible and the foundation repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk3OpeningsY | (Gravity Tanks) Are there any unprotected openings in the tank (breaches, leaks, etc)? | Storage tank not sealed*. (see photo #) Other than the openings afforded by the #24-mesh screens on the vents and overflows, all openings must be sealed completely to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. [Describe specific openings such as: All openings between the roof and sidewalls must be sealed and watertight. Any openings from antennas, telemetry, and other appurtenances must be sealed and watertight.] |
| gvTk3InspectedN | (Gravity Tanks) If the tank is more than 10 years old, was it cleaned and inspected within the last 10 years? | Storage tank not cleaned and inspected within the last 10 years. The tank must be cleaned and inspected. Please see the enclosed Finished Water Storage Tank Inspection/Cleaning Checklist for a list of items that must be evaluated during the inspection. Tanks need to be periodically cleaned and inspected to prevent the growth of potentially harmful pathogens in the accumulated sediments and to address construction issues before they require major repairs. Inspections and cleaning may be done by a third-party professional or appropriately trained in-house staff. Please be aware that some tanks may be considered as confined spaces or hazardous environments; personnel working in or near the tanks should have all OSHA-required training, and proper safety equipment and procedures should be used at all times. After inspection and cleaning the tank must be disinfected according to AWWA standards (C652-92: Disinfection of Water Storage Facilities). In order to correct this significant deficiency, you must provide EPA with the following documentation: A completed copy of the Finished Water Storage Tank Inspection/Cleaning Checklist. A copy of inspection results and labeled photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk3OvFlSepN | (Gravity Tanks) Does the tank have an overflow separate from the vent? @ | No overflow on finished water storage tank*. In order to protect the integrity of the tank in the case of control system failure leading to overfilling, the tank must have an overflow that is separate from the vent. |
| gvTk3OvFlAccessN | (Gravity Tanks) Is the overflow accessible for inspection? | Unknown integrity of storage tank overflow [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank overflow [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. The EPA will review the inspection report and may require additional corrective actions. |
| gvTk3OvFl24MeshN | (Gravity Tanks) Overflow has a #24-mesh screen OR a duckbill valve OR a properly sealed flapper valve with screen inside (The EPA recommends a #24-mesh screen)? | Overflow screening on finished water storage tank improvement needed*. (see photo #) Overflows must be fitted with non-corrodible #24-mesh screen, or a properly sealed flapper or duckbill valve to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the pipe at a location least susceptible to vandalism. When a flapper valve is used, a screen must be placed inside the valve (EPA Region 8 recommends non-corrodible #24-mesh screen be used). In cold climates, use of a flapper or duckbill valve should be considered to minimize air movement and hence ice formation in the tank. In cold climates, provisions should be considered to prevent the flapper or duckbill from freezing shut. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk3OvFlTerm12InN | (Gravity Tanks) Does the overflow line terminate no less than 12 inches but no more than 24 inches above the ground surface? | Overflow on finished water storage tank discharges at improper height*. (see photo #) Overflow must be piped to an elevation between 12 and 24 inches above the ground surface and discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk3OvDrainStructN | (Gravity Tanks) Does the overflow discharge over an inlet structure, splash plate, or engineered rip-rap? | Overflow discharge point on finished water storage tank improvement needed*. (see photo #) Overflow must discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk3OvFlConnSewerN | (Gravity Tanks) Does the overflow have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Overflow on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain. (see photo #) No overflow may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the overflow pipe terminates at least three pipe diameters above the ground level at the sewer or storm drain, or over a splash pad. |
| gvTk3DLAccessblN | (Gravity Tanks) Is the drain accessible for inspection? | Unknown integrity of storage tank drain [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank drain [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk3DLAirGapN | (Gravity Tanks) Does the drain pipe have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Drain on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain*. (see photo #) No drain may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the drain pipe terminates at least three pipe diameters above the ground level at the sewer drain, storm drain, splash pad or engineered rip-rap. |
| gvTk3VentSepN | (Gravity Tanks) Does the tank have a vent separate from the overflow? | No vent on finished water storage tank*. In order to protect the structural integrity of the tank during changes to tank water levels, and other events affecting the confined air space, the tank must have a vent that is separate from the overflow. |
| gvTk3AirVentAccessN | (Gravity Tanks) Is the vent accessible for inspection? | Unknown integrity of storage tank air vent [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank air vent [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. The EPA will review the inspection report and may require additional corrective actions. |
| gvTk3AirVntMeshN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Is there #24-mesh screen? | Air vent screening on finished water storage tank needs improvement*. (see photo #) The vent must be fitted with non-corrodible #24-mesh screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. Prior to installing the screen, the PWS should evaluate whether the tank needs a vacuum/pressure relief valve or another mechanism to prevent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk3AirVnt24AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Downturned vent: Is the vent at least 24“ above the roof? | Downturned air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24” above the tank surface to prevent inhalation of contaminants by the tank. |
| gvTk3AirVentSoldCovN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is there a solid cover down to the bottom of the vent screen? | Air vent on finished water storage tank does not have a solid cover*. (see photo #) For non-downturned vents, the screen must have a solid cover down to the bottom of the vent screen to prevent rain and snow, and minimize dust and sunlight, from entering the tank. If the cover is installed in a manner that restricts the size of the vent opening it may result in insufficient airflow and subsequent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require evaluation by a licensed engineer to ensure that no damage will occur to the existing water tank as a result of the modifications. For elevated tanks and standpipes, the EPA strongly recommends that the system install a vent with an automatic re-setting vacuum/pressure relief mechanism if one is not already in place. |
| gvTk3AirVnt8AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is the screen at least 8” above the roof surface? | Air vent on finished water storage tank is not elevated above the roof at the required height*. (see photo #) For non-downturned vents, the bottom of the vent screen must be at least 8” above the tank roof to prevent inhalation of contaminants by the tank. |
| gvTk3AirVen24MeshN | (Gravity Tanks) Below Ground (buried or partially buried) Is air vent covered with #24-mesh screen? | Air vent screening on finished water storage tank improvement needed*. (see photo #) The vent must be fitted with non-corrodible #24-mesh screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk3AirVnTermDwnN | (Gravity Tanks) Below Ground (buried or partially buried) Does the air vent terminate downward? | Air vent on finished water storage tank does not terminate in a downturned position*. (see photo #) On buried or partially buried tanks the air vent must terminate in a downturned position. |
| gvTk3AirVnTrmAbvRfN | (Gravity Tanks) Below Ground (buried or partially buried) Is the air vent at least 24” above the roof or ground surface (whichever is higher)? | Air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24 inches above the roof or ground surface (whichever is higher) to prevent rain from entering and to prevent inhalation of contaminants by the tank. |
| gvTk3AHAccessableN | (Gravity Tanks) Is the hatch accessible for inspection? | Unknown integrity of storage tank access hatch [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank access hatch [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. The EPA will review the inspection report and may require additional corrective actions. |
| gvTk3bgAH24AboveRfN | (Gravity Tanks) For below ground tanks where the roof is completely buried, is the hatch raised at least 24” above ground level? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the ground surface. |
| gvTk3pbAH24AboveRfN | (Gravity Tanks) For partially buried tanks where the roof is visible, is the hatch raised at least 24” above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the surface of the roof. |
| gvTk3agAH4AboveRfN | (Gravity Tanks) For above ground tanks (ground level or elevated/standpipe): Is the hatch raised 4“ above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be framed at least four inches above the surface of the roof. |
| gvTk3AHShoeBxLidN | (Gravity Tanks) Does the hatch have a shoe box lid? | Hatch on Finished Water Storage Tank does not have a shoe box lid*. (see photo #) The tank hatch must be fitted with a solid watertight cover which extends down around the frame at least two inches. |
| gvTk3AHRubberGaskN | (Gravity Tanks) Is the lid tight and sealed with a rubber gasket? | Hatch on Finished Water Storage Tank does not have a gasket that creates a watertight seal. (see photo #) The tank hatch must have a rubber gasket to seal the hatch lid to the frame tightly to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| gvTk3AHALockedN | (Gravity Tanks) Is the hatch locked? | Hatch on Finished Water Storage Tank does not have a locking device. (see photo #) The cover must have a locking device. |
| gvTk4FloodingY | (Gravity Tanks) Is the site subject to flooding? | Storage tank located in an area subject to flooding. (see photo # ) [insert site specific problem and remedy] |
| gvTk4PropMaintN | (Gravity Tanks) Does the tank appear structurally sound? | Storage tank not structurally sound or properly maintained*. (see photo # ) The storage tank does not appear to be structurally sound. Specifically, the [tank component] of the tank must be evaluated by a professional engineer familiar with the construction of water-storage tanks to determine the integrity of the tank’s [tank component]. Failure to maintain the structural and sanitary integrity of the tank could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank must be made as soon as possible and it must be repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk4FounStrucSoundN | (Gravity Tanks) Does the foundation appear structurally sound? | Storage tank foundation does not appear to be structurally sound*. (see photo # ) The storage tank foundation does not appear to be structurally sound. It must be evaluated by a professional engineer familiar with the construction of water-storage tanks. Failure to maintain the structural and sanitary integrity of the tank foundation could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank foundation must be made as soon as possible and the foundation repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk4OpeningsY | (Gravity Tanks) Are there any unprotected openings in the tank (breaches, leaks, etc)? | Storage tank not sealed*. (see photo #) Other than the openings afforded by the #24-mesh screens on the vents and overflows, all openings must be sealed completely to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. [Describe specific openings such as: All openings between the roof and sidewalls must be sealed and watertight. Any openings from antennas, telemetry, and other appurtenances must be sealed and watertight.] |
| gvTk4InspectedN | (Gravity Tanks) If the tank is more than 10 years old, was it cleaned and inspected within the last 10 years? | Storage tank not cleaned and inspected within the last 10 years. The tank must be cleaned and inspected. Please see the enclosed Finished Water Storage Tank Inspection/Cleaning Checklist for a list of items that must be evaluated during the inspection. Tanks need to be periodically cleaned and inspected to prevent the growth of potentially harmful pathogens in the accumulated sediments and to address construction issues before they require major repairs. Inspections and cleaning may be done by a third-party professional or appropriately trained in-house staff. Please be aware that some tanks may be considered as confined spaces or hazardous environments; personnel working in or near the tanks should have all OSHA-required training, and proper safety equipment and procedures should be used at all times. After inspection and cleaning the tank must be disinfected according to AWWA standards (C652-92: Disinfection of Water Storage Facilities). In order to correct this significant deficiency, you must provide EPA with the following documentation: A completed copy of the Finished Water Storage Tank Inspection/Cleaning Checklist. A copy of inspection results and labeled photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk4OvFlSepN | (Gravity Tanks) Does the tank have an overflow separate from the vent? @ | No overflow on finished water storage tank*. In order to protect the integrity of the tank in the case of control system failure leading to overfilling, the tank must have an overflow that is separate from the vent. |
| gvTk4OvFlAccessN | (Gravity Tanks) Is the overflow accessible for inspection? | Unknown integrity of storage tank overflow [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank overflow [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk4OvFl24MeshN | (Gravity Tanks) Overflow has a #24-mesh screen OR a duckbill valve OR a properly sealed flapper valve with screen inside (The EPA recommends a #24-mesh screen)? | Overflow screening on finished water storage tank improvement needed*. (see photo #) Overflows must be fitted with non-corrodible #24-mesh screen, or a properly sealed flapper or duckbill valve to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the pipe at a location least susceptible to vandalism. When a flapper valve is used, a screen must be placed inside the valve (EPA Region 8 recommends non-corrodible #24-mesh screen be used). In cold climates, use of a flapper or duckbill valve should be considered to minimize air movement and hence ice formation in the tank. In cold climates, provisions should be considered to prevent the flapper or duckbill from freezing shut. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk4OvFlTerm12InN | (Gravity Tanks) Does the overflow line terminate no less than 12 inches but no more than 24 inches above the ground surface? | Overflow on finished water storage tank discharges at improper height*. (see photo #) Overflow must be piped to an elevation between 12 and 24 inches above the ground surface and discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk4OvDrainStructN | (Gravity Tanks) Does the overflow discharge over an inlet structure, splash plate, or engineered rip-rap? | Overflow discharge point on finished water storage tank improvement needed*. (see photo #) Overflow must discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk4OvFlConnSewerN | (Gravity Tanks) Does the overflow have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Overflow on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain. (see photo #) No overflow may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the overflow pipe terminates at least three pipe diameters above the ground level at the sewer or storm drain, or over a splash pad. |
| gvTk4DLAccessblN | (Gravity Tanks) Is the drain accessible for inspection? | Unknown integrity of storage tank drain [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank drain [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk4DLAirGapN | (Gravity Tanks) Does the drain pipe have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Drain on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain*. (see photo #) No drain may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the drain pipe terminates at least three pipe diameters above the ground level at the sewer drain, storm drain, splash pad or engineered rip-rap. |
| gvTk4VentSepN | (Gravity Tanks) Does the tank have a vent separate from the overflow? | No vent on finished water storage tank*. In order to protect the structural integrity of the tank during changes to tank water levels, and other events affecting the confined air space, the tank must have a vent that is separate from the overflow. |
| gvTk4AirVentAccessN | (Gravity Tanks) Is the vent accessible for inspection? | Unknown integrity of storage tank air vent [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank air vent [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. The EPA will review the inspection report and may require additional corrective actions. |
| gvTk4AirVntMeshN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Is there #24-mesh screen? | Air vent screening on finished water storage tank needs improvement*. (see photo #) The vent must be fitted with non-corrodible #24-mesh screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. Prior to installing the screen, the PWS should evaluate whether the tank needs a vacuum/pressure relief valve or another mechanism to prevent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk4AirVnt24AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Downturned vent: Is the vent at least 24“ above the roof? | Downturned air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24” above the tank surface to prevent inhalation of contaminants by the tank. |
| gvTk4AirVentSoldCovN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is there a solid cover down to the bottom of the vent screen? | Air vent on finished water storage tank does not have a solid cover*. (see photo #) For non-downturned vents, the screen must have a solid cover down to the bottom of the vent screen to prevent rain and snow, and minimize dust and sunlight, from entering the tank. If the cover is installed in a manner that restricts the size of the vent opening it may result in insufficient airflow and subsequent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require evaluation by a licensed engineer to ensure that no damage will occur to the existing water tank as a result of the modifications. For elevated tanks and standpipes, the EPA strongly recommends that the system install a vent with an automatic re-setting vacuum/pressure relief mechanism if one is not already in place. |
| gvTk4AirVnt8AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is the screen at least 8” above the roof surface? | Air vent on finished water storage tank is not elevated above the roof at the required height*. (see photo #) For non-downturned vents, the bottom of the vent screen must be at least 8” above the tank roof to prevent inhalation of contaminants by the tank. |
| gvTk4AirVen24MeshN | (Gravity Tanks) Below Ground (buried or partially buried) Is air vent covered with #24-mesh screen? | Air vent screening on finished water storage tank improvement needed*. (see photo #) The vent must be fitted with a #24-mesh non corrodible screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. |
| gvTk4AirVnTermDwnN | (Gravity Tanks) Below Ground (buried or partially buried) Does the air vent terminate downward? | Air vent on finished water storage tank does not terminate in a downturned position*. (see photo #) On buried or partially buried tanks the air vent must terminate in a downturned position. |
| gvTk4AirVnTrmAbvRfN | (Gravity Tanks) Below Ground (buried or partially buried) Is the air vent at least 24” above the roof or ground surface (whichever is higher)? | Air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24 inches above the roof or ground surface (whichever is higher) to prevent rain from entering and to prevent inhalation of contaminants by the tank. |
| gvTk4AHAccessableN | (Gravity Tanks) Is the hatch accessible for inspection? | Unknown integrity of storage tank access hatch [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank access hatch [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. The EPA will review the inspection report and may require additional corrective actions. |
| gvTk4bgAH24AboveRfN | (Gravity Tanks) For below ground tanks where the roof is completely buried, is the hatch raised at least 24” above ground level? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the ground surface. |
| gvTk4pbAH24AboveRfN | (Gravity Tanks) For partially buried tanks where the roof is visible, is the hatch raised at least 24” above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the surface of the roof. |
| gvTk4agAH4AboveRfN | (Gravity Tanks) For above ground tanks (ground level or elevated/standpipe): Is the hatch raised 4“ above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be framed at least four inches above the surface of the roof. |
| gvTk4AHShoeBxLidN | (Gravity Tanks) Does the hatch have a shoe box lid? | Hatch on Finished Water Storage Tank does not have a shoe box lid*. (see photo #) The tank hatch must be fitted with a solid watertight cover which extends down around the frame at least two inches. |
| gvTk4AHRubberGaskN | (Gravity Tanks) Is the lid tight and sealed with a rubber gasket? | Hatch on Finished Water Storage Tank does not have a gasket that creates a watertight seal. (see photo #) The tank hatch must have a rubber gasket to seal the hatch lid to the frame tightly to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| gvTk4AHALockedN | (Gravity Tanks) Is the hatch locked? | Hatch on Finished Water Storage Tank does not have a locking device. (see photo #) The cover must have a locking device. |
| gvTk5FloodingY | (Gravity Tanks) Is the site subject to flooding? | Storage tank located in an area subject to flooding. (see photo # ) [insert site specific problem and remedy] |
| gvTk5PropMaintN | (Gravity Tanks) Does the tank appear structurally sound? | Storage tank not structurally sound or properly maintained*. (see photo # ) The storage tank does not appear to be structurally sound. Specifically, the [tank component] of the tank must be evaluated by a professional engineer familiar with the construction of water-storage tanks to determine the integrity of the tank’s [tank component]. Failure to maintain the structural and sanitary integrity of the tank could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank must be made as soon as possible and it must be repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk5FounStrucSoundN | (Gravity Tanks) Does the foundation appear structurally sound? | Storage tank foundation does not appear to be structurally sound*. (see photo # ) The storage tank foundation does not appear to be structurally sound. It must be evaluated by a professional engineer familiar with the construction of water-storage tanks. Failure to maintain the structural and sanitary integrity of the tank foundation could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank foundation must be made as soon as possible and the foundation repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk5OpeningsY | (Gravity Tanks) Are there any unprotected openings in the tank (breaches, leaks, etc)? | Storage tank not sealed*. (see photo #) Other than the openings afforded by the #24-mesh screens on the vents and overflows, all openings must be sealed completely to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. [Describe specific openings such as: All openings between the roof and sidewalls must be sealed and watertight. Any openings from antennas, telemetry, and other appurtenances must be sealed and watertight.] |
| gvTk5InspectedN | (Gravity Tanks) If the tank is more than 10 years old, was it cleaned and inspected within the last 10 years? | Storage tank not cleaned and inspected within the last 10 years. The tank must be cleaned and inspected. Please see the enclosed Finished Water Storage Tank Inspection/Cleaning Checklist for a list of items that must be evaluated during the inspection. Tanks need to be periodically cleaned and inspected to prevent the growth of potentially harmful pathogens in the accumulated sediments and to address construction issues before they require major repairs. Inspections and cleaning may be done by a third-party professional or appropriately trained in-house staff. Please be aware that some tanks may be considered as confined spaces or hazardous environments; personnel working in or near the tanks should have all OSHA-required training, and proper safety equipment and procedures should be used at all times. After inspection and cleaning the tank must be disinfected according to AWWA standards (C652-92: Disinfection of Water Storage Facilities). In order to correct this significant deficiency, you must provide EPA with the following documentation: A completed copy of the Finished Water Storage Tank Inspection/Cleaning Checklist. A copy of inspection results and labeled photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk5OvFlSepN | (Gravity Tanks) Does the tank have an overflow separate from the vent? @ | No overflow on finished water storage tank*. In order to protect the integrity of the tank in the case of control system failure leading to overfilling, the tank must have an overflow that is separate from the vent. |
| gvTk5OvFlAccessN | (Gravity Tanks) Is the overflow accessible for inspection? | Unknown integrity of storage tank overflow [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank overflow [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk5OvFl24MeshN | (Gravity Tanks) Overflow has a #24-mesh screen OR a duckbill valve OR a properly sealed flapper valve with screen inside (The EPA recommends a #24-mesh screen)? | Overflow screening on finished water storage tank improvement needed*. (see photo #) Overflows must be fitted with non-corrodible #24-mesh screen, or a properly sealed flapper or duckbill valve to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the pipe at a location least susceptible to vandalism. When a flapper valve is used, a screen must be placed inside the valve (EPA Region 8 recommends non-corrodible #24-mesh screen be used). In cold climates, use of a flapper or duckbill valve should be considered to minimize air movement and hence ice formation in the tank. In cold climates, provisions should be considered to prevent the flapper or duckbill from freezing shut. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk5OvFlTerm12InN | (Gravity Tanks) Does the overflow line terminate no less than 12 inches but no more than 24 inches above the ground surface? | Overflow on finished water storage tank discharges at improper height*. (see photo #) Overflow must be piped to an elevation between 12 and 24 inches above the ground surface and discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk5OvDrainStructN | (Gravity Tanks) Does the overflow discharge over an inlet structure, splash plate, or engineered rip-rap? | Overflow discharge point on finished water storage tank improvement needed*. (see photo #) Overflow must discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk5OvFlConnSewerN | (Gravity Tanks) Does the overflow have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Overflow on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain. (see photo #) No overflow may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the overflow pipe terminates at least three pipe diameters above the ground level at the sewer or storm drain, or over a splash pad. |
| gvTk5DLAccessblN | (Gravity Tanks) Is the drain accessible for inspection? | Unknown integrity of storage tank drain [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank drain [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk5DLAirGapN | (Gravity Tanks) Does the drain pipe have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Drain on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain*. (see photo #) No drain may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the drain pipe terminates at least three pipe diameters above the ground level at the sewer drain, storm drain, splash pad or engineered rip-rap. |
| gvTk5VentSepN | (Gravity Tanks) Does the tank have a vent separate from the overflow? | No vent on finished water storage tank*. In order to protect the structural integrity of the tank during changes to tank water levels, and other events affecting the confined air space, the tank must have a vent that is separate from the overflow. |
| gvTk5AirVentAccessN | (Gravity Tanks) Is the vent accessible for inspection? | Unknown integrity of storage tank air vent [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank air vent [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. The EPA will review the inspection report and may require additional corrective actions. |
| gvTk5AirVntMeshN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Is there #24-mesh screen? | Air vent screening on finished water storage tank needs improvement*. (see photo #) The vent must be fitted with non-corrodible #24-mesh screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. Prior to installing the screen, the PWS should evaluate whether the tank needs a vacuum/pressure relief valve or another mechanism to prevent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk5AirVnt24AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Downturned vent: Is the vent at least 24“ above the roof? | Downturned air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24” above the tank surface to prevent inhalation of contaminants by the tank. |
| gvTk5AirVentSoldCovN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is there a solid cover down to the bottom of the vent screen? | Air vent on finished water storage tank does not have a solid cover*. (see photo #) For non-downturned vents, the screen must have a solid cover down to the bottom of the vent screen to prevent rain and snow, and minimize dust and sunlight, from entering the tank. If the cover is installed in a manner that restricts the size of the vent opening it may result in insufficient airflow and subsequent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require evaluation by a licensed engineer to ensure that no damage will occur to the existing water tank as a result of the modifications. For elevated tanks and standpipes, the EPA strongly recommends that the system install a vent with an automatic re-setting vacuum/pressure relief mechanism if one is not already in place. |
| gvTk5AirVnt8AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is the screen at least 8” above the roof surface? | Air vent on finished water storage tank is not elevated above the roof at the required height*. (see photo #) For non-downturned vents, the bottom of the vent screen must be at least 8” above the tank roof to prevent inhalation of contaminants by the tank. |
| gvTk5AirVen24MeshN | (Gravity Tanks) Below Ground (buried or partially buried) Is air vent covered with #24-mesh screen? | Air vent screening on finished water storage tank improvement needed*. (see photo #) The vent must be fitted with non-corrodible #24-mesh screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk5AirVnTermDwnN | (Gravity Tanks) Below Ground (buried or partially buried) Does the air vent terminate downward? | Air vent on finished water storage tank does not terminate in a downturned position*. (see photo #) On buried or partially buried tanks the air vent must terminate in a downturned position. |
| gvTk5AirVnTrmAbvRfN | (Gravity Tanks) Below Ground (buried or partially buried) Is the air vent at least 24” above the roof or ground surface (whichever is higher)? | Air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24 inches above the roof or ground surface (whichever is higher) to prevent rain from entering and to prevent inhalation of contaminants by the tank. |
| gvTk5AHAccessableN | (Gravity Tanks) Is the hatch accessible for inspection? | Unknown integrity of storage tank access hatch [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank access hatch [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. The EPA will review the inspection report and may require additional corrective actions. |
| gvTk5bgAH24AboveRfN | (Gravity Tanks) For below ground tanks where the roof is completely buried, is the hatch raised at least 24” above ground level? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the ground surface. |
| gvTk5pbAH24AboveRfN | (Gravity Tanks) For partially buried tanks where the roof is visible, is the hatch raised at least 24” above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the surface of the roof. |
| gvTk5agAH4AboveRfN | (Gravity Tanks) For above ground tanks (ground level or elevated/standpipe): Is the hatch raised 4“ above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be framed at least four inches above the surface of the roof. |
| gvTk5AHShoeBxLidN | (Gravity Tanks) Does the hatch have a shoe box lid? | Hatch on Finished Water Storage Tank does not have a shoe box lid*. (see photo #) The tank hatch must be fitted with a solid watertight cover which extends down around the frame at least two inches. |
| gvTk5AHRubberGaskN | (Gravity Tanks) Is the lid tight and sealed with a rubber gasket? | Hatch on Finished Water Storage Tank does not have a gasket that creates a watertight seal. (see photo #) The tank hatch must have a rubber gasket to seal the hatch lid to the frame tightly to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| gvTk5AHALockedN | (Gravity Tanks) Is the hatch locked? | Hatch on Finished Water Storage Tank does not have a locking device. (see photo #) The cover must have a locking device. |
| gvTk6FloodingY | (Gravity Tanks) Is the site subject to flooding? | Storage tank located in an area subject to flooding. (see photo # ) [insert site specific problem and remedy] |
| gvTk6PropMaintN | (Gravity Tanks) Does the tank appear structurally sound? | Storage tank not structurally sound or properly maintained*. (see photo # ) The storage tank does not appear to be structurally sound. Specifically, the [tank component] of the tank must be evaluated by a professional engineer familiar with the construction of water-storage tanks to determine the integrity of the tank’s [tank component]. Failure to maintain the structural and sanitary integrity of the tank could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank must be made as soon as possible and it must be repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk6FounStrucSoundN | (Gravity Tanks) Does the foundation appear structurally sound? | Storage tank foundation does not appear to be structurally sound*. (see photo # ) The storage tank foundation does not appear to be structurally sound. It must be evaluated by a professional engineer familiar with the construction of water-storage tanks. Failure to maintain the structural and sanitary integrity of the tank foundation could lead directly to contamination within the tank, illness and/or the loss of property. The professional evaluation of the storage tank foundation must be made as soon as possible and the foundation repaired if necessary to ensure the structural integrity and reliability of the tank. |
| gvTk6OpeningsY | (Gravity Tanks) Are there any unprotected openings in the tank (breaches, leaks, etc)? | Storage tank not sealed*. (see photo #) Other than the openings afforded by the #24-mesh screens on the vents and overflows, all openings must be sealed completely to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. [Describe specific openings such as: All openings between the roof and sidewalls must be sealed and watertight. Any openings from antennas, telemetry, and other appurtenances must be sealed and watertight.] |
| gvTk6InspectedN | (Gravity Tanks) If the tank is more than 10 years old, was it cleaned and inspected within the last 10 years? | Storage tank not cleaned and inspected within the last 10 years. The tank must be cleaned and inspected. Please see the enclosed Finished Water Storage Tank Inspection/Cleaning Checklist for a list of items that must be evaluated during the inspection. Tanks need to be periodically cleaned and inspected to prevent the growth of potentially harmful pathogens in the accumulated sediments and to address construction issues before they require major repairs. Inspections and cleaning may be done by a third-party professional or appropriately trained in-house staff. Please be aware that some tanks may be considered as confined spaces or hazardous environments; personnel working in or near the tanks should have all OSHA-required training, and proper safety equipment and procedures should be used at all times. After inspection and cleaning the tank must be disinfected according to AWWA standards (C652-92: Disinfection of Water Storage Facilities). In order to correct this significant deficiency, you must provide EPA with the following documentation: A completed copy of the Finished Water Storage Tank Inspection/Cleaning Checklist. A copy of inspection results and labeled photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk6OvFlSepN | (Gravity Tanks) Does the tank have an overflow separate from the vent? @ | No overflow on finished water storage tank*. In order to protect the integrity of the tank in the case of control system failure leading to overfilling, the tank must have an overflow that is separate from the vent. |
| gvTk6OvFlAccessN | (Gravity Tanks) Is the overflow accessible for inspection? | Unknown integrity of storage tank overflow [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank overflow [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk6OvFl24MeshN | (Gravity Tanks) Overflow has a #24-mesh screen OR a duckbill valve OR a properly sealed flapper valve with screen inside (the EPA recommends a #24-mesh screen)? | Overflow screening on finished water storage tank improvement needed*. (see photo #) Overflows must be fitted with non-corrodible #24-mesh screen, or a properly sealed flapper or duckbill valve to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the pipe at a location least susceptible to vandalism. When a flapper valve is used, a screen must be placed inside the valve (EPA Region 8 recommends non-corrodible #24-mesh screen be used). In cold climates, use of a flapper or duckbill valve should be considered to minimize air movement and hence ice formation in the tank. In cold climates, provisions should be considered to prevent the flapper or duckbill from freezing shut. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk6OvFlTerm12InN | (Gravity Tanks) Does the overflow line terminate no less than 12 inches but no more than 24 inches above the ground surface? | Overflow on finished water storage tank discharges at improper height*. (see photo #) Overflow must be piped to an elevation between 12 and 24 inches above the ground surface and discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk6OvDrainStructN | (Gravity Tanks) Does the overflow discharge over an inlet structure, splash plate, or engineered rip-rap? | Overflow discharge point on finished water storage tank improvement needed*. (see photo #) Overflow must discharge over a drainage inlet structure, splash plate, or engineered rip-rap. |
| gvTk6OvFlConnSewerN | (Gravity Tanks) Does the overflow have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Overflow on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain. (see photo #) No overflow may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the overflow pipe terminates at least three pipe diameters above the ground level at the sewer or storm drain, or over a splash pad. |
| gvTk6DLAccessblN | (Gravity Tanks) Is the drain accessible for inspection? | Unknown integrity of storage tank drain [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank drain [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. EPA will review the inspection report and may require additional corrective actions. |
| gvTk6DLAirGapN | (Gravity Tanks) Does the drain pipe have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewer? | Drain on finished water storage tank is directly connected to a sanitary sewer, combined sewer or storm sewer drain*. (see photo #) No drain may be directly connected to a sanitary sewer, combined sewer or storm sewer drain. An air gap must be present such that the drain pipe terminates at least three pipe diameters above the ground level at the sewer drain, storm drain, splash pad or engineered rip-rap. |
| gvTk6VentSepN | (Gravity Tanks) Does the tank have a vent separate from the overflow? | No vent on finished water storage tank*. In order to protect the structural integrity of the tank during changes to tank water levels, and other events affecting the confined air space, the tank must have a vent that is separate from the overflow. |
| gvTk6AirVentAccessN | (Gravity Tanks) Is the vent accessible for inspection? | Unknown integrity of storage tank air vent [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank air vent [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. The EPA will review the inspection report and may require additional corrective actions. |
| gvTk6AirVntMeshN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Is there #24-mesh screen? | Air vent screening on finished water storage tank needs improvement*. (see photo #) The vent must be fitted with non-corrodible #24-mesh screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. Prior to installing the screen, the PWS should evaluate whether the tank needs a vacuum/pressure relief valve or another mechanism to prevent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk6AirVnt24AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) Downturned vent: Is the vent at least 24“ above the roof? | Downturned air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24” above the tank surface to prevent inhalation of contaminants by the tank. |
| gvTk6AirVentSoldCovN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is there a solid cover down to the bottom of the vent screen? | Air vent on finished water storage tank does not have a solid cover*. (see photo #) For non-downturned vents, the screen must have a solid cover down to the bottom of the vent screen to prevent rain and snow, and minimize dust and sunlight, from entering the tank. If the cover is installed in a manner that restricts the size of the vent opening it may result in insufficient airflow and subsequent damage to the tank. Correction of this deficiency will require a permit to construct from the WYDEQ and will require evaluation by a licensed engineer to ensure that no damage will occur to the existing water tank as a result of the modifications. For elevated tanks and standpipes, the EPA strongly recommends that the system install a vent with an automatic re-setting vacuum/pressure relief mechanism if one is not already in place. |
| gvTk6AirVnt8AbvRfN | (Gravity Tanks) Above Ground (ground level or elevated / standpipe) For non-downturned vents: Is the screen at least 8” above the roof surface? | Air vent on finished water storage tank is not elevated above the roof at the required height*. (see photo #) For non-downturned vents, the bottom of the vent screen must be at least 8” above the tank roof to prevent inhalation of contaminants by the tank. |
| gvTk6AirVen24MeshN | (Gravity Tanks) Below Ground (buried or partially buried) Is air vent covered with #24-mesh screen? | Air vent screening on finished water storage tank improvement needed*. (see photo #) The vent must be fitted with non-corrodible #24-mesh screen to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. The screen should preferably be installed within the vent at a location least susceptible to vandalism. Correction of this deficiency will require a permit to construct from the WYDEQ and will require an evaluation by an engineering firm to ensure that no damage will occur to the existing water tank as a result of the modifications to address the significant deficiencies. |
| gvTk6AirVnTermDwnN | (Gravity Tanks) Below Ground (buried or partially buried) Does the air vent terminate downward? | Air vent on finished water storage tank does not terminate in a downturned position*. (see photo #) On buried or partially buried tanks the air vent must terminate in a downturned position. |
| gvTk6AirVnTrmAbvRfN | (Gravity Tanks) Below Ground (buried or partially buried) Is the air vent at least 24” above the roof or ground surface (whichever is higher)? | Air vent on finished water storage tank does not terminate at required height*. (see photo #) The vent must terminate in an inverted U construction at least 24 inches above the roof or ground surface (whichever is higher) to prevent rain from entering and to prevent inhalation of contaminants by the tank. |
| gvTk6AHAccessableN | (Gravity Tanks) Is the hatch accessible for inspection? | Unknown integrity of storage tank access hatch [add other inaccessible components to consolidate language]. The sanitary surveyor was unable to evaluate the tank access hatch [add other components to consolidate], and the water system was not able to produce documentation of the condition of these components. Each item that could not be inspected during the sanitary survey must be inspected and the structure/condition must be compared to the enclosed Tech Tips for Finished Water Storage Facilities to determine if corrective action is needed. Tank inspectors can be third-party professionals or appropriately trained in-house staff. In order to correct this significant deficiency you must provide the EPA with the following documentation: A completed copy of the Unknown Integrity Checklist. A copy of the inspection report. The inspection report must describe the condition of each specified tank component and include photographs. The date that any corrective actions needed to address deficiencies with the tank components will be completed. The EPA will review the inspection report and may require additional corrective actions. |
| gvTk6bgAH24AboveRfN | (Gravity Tanks) For below ground tanks where the roof is completely buried, is the hatch raised at least 24” above ground level? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the ground surface. |
| gvTk6pbAH24AboveRfN | (Gravity Tanks) For partially buried tanks where the roof is visible, is the hatch raised at least 24” above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be elevated a minimum of 24 inches above the surface of the roof. |
| gvTk6agAH4AboveRfN | (Gravity Tanks) For above ground tanks (ground level or elevated/standpipe): Is the hatch raised 4“ above the roof? @ | Hatch on Finished Water Storage Tank is not elevated to the required height*. (see photo #) The tank hatch must be framed at least four inches above the surface of the roof. |
| gvTk6AHShoeBxLidN | (Gravity Tanks) Does the hatch have a shoe box lid? | Hatch on Finished Water Storage Tank does not have a shoe box lid*. (see photo #) The tank hatch must be fitted with a solid watertight cover which extends down around the frame at least two inches. |
| gvTk6AHRubberGaskN | (Gravity Tanks) Is the lid tight and sealed with a rubber gasket? | Hatch on Finished Water Storage Tank does not have a gasket that creates a watertight seal. (see photo #) The tank hatch must have a rubber gasket to seal the hatch lid to the frame tightly to prevent contamination (including contamination carried by insects, rodents, and birds) from entering the water system. |
| gvTk6AHALockedN | (Gravity Tanks) Is the hatch locked? | Hatch on Finished Water Storage Tank does not have a locking device. (see photo #) The cover must have a locking device. |
| swEpichlorohidrinY | (SW Treatment) Does the system use a chemical containing epichlorohydrin or polyacrylamide that is dosed in excess of the NSF 60 Max Allowable Dose? | System has a potential violation for excess dosing of a chemical that contains epichlorohydrin or polyacrylamide (141.111). |
| filtPrLocationEPAN | (SW Treatment) Does the location of the CFE turbidimeter comply with EPA policy SWTR #5? | Combined Filter Effluent (CFE) turbidity monitoring location is not representative of the filtered water*. The system’s finished water (CFE) turbidimeter sampling location is not representative of the filtered water. [describe system specific situation and remedy] |
| swTurbimCalibrateN | (SW Treatment) Are turbidimeters calibrated at least once every quarter? | Turbidimeters Must Be Calibrated Quarterly. Turbidity is used to measure filtration effectiveness, and incorrect turbidity monitoring has the potential to allow contamination to pass into the finished water. The Long Term 1 Enhanced Surface Water Treatment Rule requires that turbidimeter calibration be conducted using procedures specified by the manufacturer. To be consistent with typical manufacturer specifications for surface water treatment plants, turbidimeters for measuring individual filter effluent (IFE) and combined filter effluent (CFE) turbidity must be calibrated at least quarterly according to manufacturer procedures using a primary standard such as formazin. |
| swPrimaryStndCalibrN | (SW Treatment) Does the system use a primary standard to perform the calibration? | Primary Standard Not Used to Calibrate Turbidimeters. Turbidity is used to measure filtration effectiveness, and incorrect turbidity monitoring has the potential to allow contamination to pass into the finished water. The Long Term 1 Enhanced Surface Water Treatment Rule requires that turbidimeter calibration be conducted using procedures specified by the manufacturer. To be consistent with typical manufacturer specifications for surface water treatment plants, turbidimeters for measuring individual filter effluent (IFE) and combined filter effluent (CFE) turbidity must be calibrated at least quarterly according to manufacturer procedures using a primary standard such as formazin. |
| swPotVioTurbRecN | (SW Treatment) Are CFE turbidity records available for the last 5 years? | System has a potential violation for failing to maintain CFE turbidity records (141.33a). |
| filtPrRec5NTUN | (SW Treatment) Can CFE turbidities be recorded up to 5 NTU? | Inadequate treatment process monitoring, recording, and recordkeeping for surface water treatment plants. The SCADA system must be able to record and store combined filter effluent (CFE) turbidity values up to at least 5 NTU. |
| filtPrBkWshTurbIdntN | (SW Treatment) (Conventional and Direct) Can turbidities associated with off-periods (backwash, FTW) be identified so they are not counted for compliance? | Inadequate Treatment Process Monitoring, Recording, and Recordkeeping for Surface Water Treatment Plants. The IFE turbidity recording method employed by the system does not adequately identify the status of the filter at the time each turbidity reading is recorded (i.e. filtering to clearwell, backwashing, filtering to waste, offline). As a result, the surveyor was not able to determine which turbidity values were valid readings that counted toward compliance. |
| convDirF24InchN | (SW Treatment) (Conventional and Direct) Total at least 24”? | Inadequate filtration design or operation. During the survey, the operators indicated that the depth of the filtration media is insufficient. The 2012 Recommended Standards for Water Works (10 States Standards) Section 4.3.1.6 Filter Material states that filter media depth for rapid sand filtration should not be less than 24 inches. |
| convDirFRateLT2gpmN | (SW Treatment) (Conventional and Direct) Is the filtration rate less than 2 gpm/sf (mono-media), 4 gpm/sf (dual media) or 6 gpm/sf (deep bed)? | Inadequate treatment process operations. Operations at the water treatment plant create the potential for sending inadequately treated water to distribution. The current operation of the filter exceeds the recommended loading rate. |
| convDirFBckWshRaw | (SW Treatment) (Conventional and Direct) What is used for a backwash? raw water | System is using raw water to backwash conventional or direct filters that are the system's final filtration barrier. (no standard language) |
| convDirFTMTurbConN | (SW Treatment) (Conventional and Direct) Does each filter have an individual effluent (IFE) turbidimeter? | System has a potential violation for failing to monitor the IFE turbidity as required by the regulations for conventional / direct filtration plants (141.560 or 141.174a)*. |
| convDirAdRecRdgN | (SW Treatment) (Conventional and Direct) Are IFE turbidities measured continuously, and recorded at least every 15 Minutes | System has a potential violation for failing to adequately record the IFE turbidity readings as required by the regulations for conventional / direct filtration plants (141.560c or 141.174a). |
| convDirIFECalibrateN | (SW Treatment) (Conventional and Direct) Is IFE turbidity recorder (SCADA or charts) calibrated to record turbidities ≥ 2 NTU? | Inadequate Treatment Process Monitoring, Recording, and Recordkeeping for Surface Water Treatment Plants The Long Term 1 Enhanced Surface Water Treatment Rule requires that the turbidity of the finished water from the individual filters be monitored continuously and recorded at least once every 15 minutes. This data is used to determine whether an individual filter effluent (IFE) turbidity exceeds either 1.0 or 2.0 NTU in two consecutive 15 minute readings, which may trigger the need for corrective actions. The IFE turbidimeters must be calibrated to record turbidity values of at least 2.0 NTU. |
| convDirFToMntIFEN | (SW Treatment) (Conventional and Direct) Are IFE records kept for the last 3 years (as applicable)? | System has a potential violation for failing to maintain IFE records for 3 years (conventional and direct filtration) (141.571a or 141.175b). |
| convDirFToRptIFETrbN | (SW Treatment) (Conventional and Direct) If so, did they report to the EPA and do a filter profile, if required? | System has a potential violation for failing to report high IFE turbidities to the EPA and conduct a filter profile (141.175b1). |
| convDirFTRSelfAssN | (SW Treatment) (Conventional and Direct) If this occurred 3 months in a row, did they conduct a filter self-assessment? | System has a potential violation for failing to report high IFE turbidity readings to the EPA and conduct a filter self-assessment following 3 months of IFE turbidity readings over 1 NTU (141.563b or 141.175b3). |
| convDirFTR2NTUN | (SW Treatment) (Conventional and Direct) If this occurred 2 months in a row for the same filter, did they report to the EPA and have a CPE performed? | System has a potential violation for failing to report to the EPA and have a CPE performed following 2 months of IFE turbidity readings over 2 NTU (141.563c or 141.175b4). |
| convDirFTRGT10KN | (SW Treatment) (Conventional and Direct) If so, did they report to the EPA and do a filter profile, if required? | System has a potential violation for failing to report high IFE turbidities to the EPA and conduct a filter profile (IESWTR - systems greater than 10,000) (141.175b2). |
| convDirExdCFELimN | (SW Treatment) (Conventional and Direct) Based on these records, has the system consistently met the CFE turbidity requirements for this type of filtration during the last 12 months? | System has a potential violation for exceeding the CFE turbidity limits for conventional or direct filtration and failing to report to the EPA (141.551a1 / 141.551b1 or 141.173a / 141.173a2). |
| convDirFTMBckWshN | (SW Treatment) (Conventional and Direct) Are records of recycle practices kept in an acceptable format for each year that includes all of the required elements? | System has a potential violation for failing to maintain the records required by the Filter Backwash Recycling Rule (141.76). |
| conDirExdTurMemN | (SW Treatment) (Membranes) Has the PWS consistently been meeting the CFE turbidity requirements for this type of filtration? | System has a potential violation for exceeding the CFE turbidity limits for membrane filtration and failing to report to the EPA (141.551a2 / 141/551b2 or 141.173b). |
| convDirDITMemN | (SW Treatment) (Membranes) Are direct integrity tests (DIT) performed at least daily (specify pressure or vacuum applied)? | Inadequate Membrane Filtration Operation resulting in Inadequate Treatment (this is a violation of 141.719b3 for systems that receive credit for additional filtration under the LT2ESWTR): Due to plant design and / or equipment problems, direct integrity tests (DIT) are not being performed on all membrane skids on a daily basis. Daily direct integrity testing is required to evaluate whether there are breaches in the membrane modules which would allow contamination to pass through to the filtered water. Membrane units that are not being assessed for integrity by daily direct integrity testing are considered cartridge filtration rather than membrane filtration. Cartridge filters are credited with only 2 logs removal of Giardia rather than the 3 logs Giardia removal credited to membrane filtration. To meet the treatment technique for 3 logs Giardia reduction of 40 CFR §141.70(a)(1) of the Surface Water Treatment Rule, cartridge filtration systems must achieve an additional 1.0 log inactivation of Giardia. As documented in the sanitary survey, under winter conditions the plant disinfection process is not able to achieve 1.0 log inactivation of Giardia at the first user. Therefore, the system must resume conducting and passing daily direct integrity tests on both membrane skids to receive the higher Giardia removal credits associated with membrane filtration. |
| convDirInadFilDesN | (SW Treatment) (Membranes) For continuous indirect integrity testing, does each unit/skid have its own online turbidimeter | Inadequate Filtration Design or Operation, resulting in Inadequate Treatment* (this is a violation of 141.719b4 for systems that receive credit for additional filtration under the LT2ESWTR): The individual membrane filtration units are not equipped with a turbidimeter that continuously samples the individual filter effluent (IFE). Membrane units that do not (1) have an individual filter turbidimeter, and (2) are not continuously monitoring turbidity from each unit with a 0.15 NTU trigger for repeat direct integrity testing, are considered cartridge filtration rather than membrane filtration. Cartridge filters are credited with only 2 logs removal of Giardia rather than the 3 logs Giardia removal credited to membrane filtration. To meet the treatment technique for 3 logs Giardia reduction of 40 CFR §141.70(a)(1) of the Surface Water Treatment Rule, cartridge filtration systems must achieve an additional 1.0 log inactivation of Giardia. As documented in the sanitary survey, the plant disinfection process does not consistently achieve 1.0 log inactivation of Giardia at the first user. Therefore, the system must install an IFE turbidimeter on each membrane unit that triggers an integrity test when the turbidity exceeds 0.15 NTU in order to receive the higher Giardia removal credits associated with membrane filtration. |
| convDirIFEMon15N | (SW Treatment) (Membranes) Is filtrate turbidity monitored continuously and recorded at least once every15 minutes? | System has a potential violation for not monitoring IFE continuously and recording values once every 15 minutes (membrane filtration) (141.719b4) (systems not receiving additional filtration credit under the LT2ESWTR - considered a significant deficiency). (no standard language) |
| convDirIFETurTr15N | Is it set with a trigger level of 0.15 NTU for > 15 minutes (a DIT should be initiated when filtrate turbidity exceeds this level)? | System has a potential violation - IFE turbidimeters not set with a trigger level of 0.15 NTU for longer than 15 minutes to initiate a DIT (membrane filtration) (141.719b4) (systems not receiving additional filtration credit under the LT2ESWTR - considered a significant deficiency). (no standard language) |
| membrOpKwChkMembrN | (SW Treatment) (Membranes) Do operators know how to check and repair membranes when a DIT fails? | System operators do not know how to check and repair membranes if a direct integrity test fails. (no standard language) |
| bgsCartExdTurbLimN | (SW Treatment) (Bags and Cartridges) Has the PWS consistently been meeting the CFE turbidity requirements for this type of filtration? | System has a potential violation for exceeding the CFE turbidity limits for bag / cartridge filtration and failing to report to the EPA (141.551a2 / 141/551b2 or 141.173b) |
| bgsCartPressGaugeN | (SW Treatment) (Bags and Cartridges) Are there working pressure gauges before and after filters? | Inadequate filtration design or operation*. Adequate microbial removal requires that a cartridge system not be used at conditions exceeding its design specifications (flow rate, inlet pressure and pressure drop), and that the cartridge be properly installed in the housing for which it was designed. The current treatment system does not have flowmeters or flow restrictors, nor pressure gauges to monitor pressure drop across the cartridges. It is unclear what the system design limitations are. The filter housings and cartridge elements should be evaluated to ensure that manufacturer’s recommended flow and pressure limits are not exceeded; flowmeters and flow restrictors should be installed as needed if the filters are not designed for the maximum flow from the intake pumps. Pressure gauges should be installed up and downstream of the cartridges to allow daily monitoring and recording of pressure drops and to trigger filter change outs when manufacturer’s limits are close to being reached. |
| bgsCartRecPressDrpN | (SW Treatment) (Bags and Cartridges) Does the PWS keep daily records of monitoring the pressure drop across the filters, and know when to change out filters? | Inadequate filtration design or operation. Adequate microbial removal requires that a cartridge system not be used at conditions exceeding its design specifications (flow rate, inlet pressure and pressure drop), and that the cartridge be properly installed in the housing for which it was designed. In order to ensure that these conditions are met, the differential pressure across the filter bags should be monitored and recorded daily and the filters should be changed out when the manufacturer’s limits are close to being reached. The system is currently not monitoring and / or recording these values on a daily basis. |
| bgsCartRemvCrytoN | (SW Treatment) (Bags and Cartridges) Has the final filter or pre/final filter combination been demonstrated to remove at least 99.9% of Cryptosporidium or equivalent size particles or have a 1 or 2 micron absolute pore size rating? | Inadequate filtration design or operation*. In order to ensure 99% removal of Cryptosporidium as required by the Long Term 1 Enhanced Surface Water Treatment Rule, the final cartridge filter must be one to two micron absolute pore size, unless the manufacturer can provide challenge testing results showing 99.9% removal of Cryptosporidium or a surrogate of the same size. According to the manufacturer, the bag filter currently being used as the final filtration barrier has not been certified for Cryptosporidium removal. The PWS should provide documentation indicating that the existing filter meets the above requirements, or use a different filter that does meet these requirements. |
| bgsCartFlowExceedY | (SW Treatment) (Bags and Cartridges) Does the flow rate through the final filter exceed the manufacturer’s maximum recommended flow rate? | Inadequate filtration design or operation*. The bag filter currently being used as the final filtration barrier is being operated at a rate that exceeds the manufacturer’s recommended maximum flow rate. Adequate microbial removal requires that a cartridge system not be used at conditions exceeding its design specifications (flow rate, inlet pressure and pressure drop). |
| bgsCartDEFilTurbN | (SW Treatment) (DE Filtration) Has the PWS consistently been meeting the CFE turbidity requirements for this type of filtration? | System has a potential violation for exceeding the CFE turbidity limits for DE filtration and failing to report to the EPA (141.551a2 / 141/551b2 or 141.173b). |
| ditEaFRateN | (SW Treatment) (DE Filtration) Is the filtration rate less than 1.5 gpm/sf? | The Diatomaceous Earth filters are being operated at a rate that exceeds 1.5 gpm/sf. (no standard language) |
| slwSndFilRateN | (SW Treatment) (Slow Sand) Is the filtration rate less than 0.1 gpm/sf? | The slow sand filters are being operated at a rate that exceeds 0.1 gpm/sf. (no standard language) |
| slwSndExdTurbLN | (SW Treatment) (Slow Sand) Has the PWS consistently been meeting the CFE turbidity requirements for this type of filtration? | System has a potential violation for exceeding the CFE turbidity limits for slow sand filtration and failing to report to the EPA (141.551a2 / 141/551b2 or 141.173b) |
| slwSndRwTurbLT10N | (SW Treatment) (Slow Sand) Is turbidity of raw water to filters always <10 NTU? | The slow sand filters are being used to treat raw water that exceeds 10 NTU. (no standard language) |
| slwSndDepthOSand3FtN | (SW Treatment) (Slow Sand) Is water depth over sand at least 3 feet during operation? | The depth of the water being maintained at the slow sand filters is less than 3 feet during operation. (no standard language) |
| slwSndHeadLossMonN | (SW Treatment) (Slow Sand) Is head loss across filters monitored and used for process control? | The system is using slow sand filters as a final filtration barrier and not monitoring the head loss for process control. (no standard language) |
| slwSndFTMUVRecN | (SW Treatment) (UV Disinfection) Does PWS keep records of UV reports sent monthly to the EPA? | System has a potential violation for failing to maintain UV operation records (141.722c) |
| uvDisFlowMeterAlarmN | (SW Treatment) (UV Disinfection <40 gpm) Is there a flow meter to monitor/alarm or a flow restrictor valve so the max flow rate is not exceeded | The system does not have a means of ensuring that the flow rate through the UV unit does not exceed the manufacturer’s maximum validated flow rate (less than 40 gpm UV). (no standard language) |
| uvDisIntensitySensN | (SW Treatment) (UV Disinfection <40 gpm) Is there an intensity sensor and alarm (visible/audible) to indicate low intensity? | The system does not have an intensity sensor alarm to indicate low UV intensity (less than 40 gpm UV). (no standard language) |
| uvDisUVStatusAlmN | (SW Treatment) (UV Disinfection <40 gpm) Is there a UV lamp status alarm (visible/audible) to indicate lamps off | The system does not have a UV lamp status alarm (less than 40 gpm UV). (no standard language) |
| uvDisLampAgeAlmN | (SW Treatment) (UV Disinfection <40 gpm) Is there a UV lamp age counter/alarm? | The system does not have a UV lamp age counter / alarm (less than 40 gpm UV). (no standard language) |
| uvDisAutoShutOffN | (SW Treatment) (UV Disinfection <40 gpm) Is there an automatic shut-off fail-safe solenoid valve so that water does not flow through the unit without adequate treatment? | The UV disinfection unit is not equipped with a fail safe solenoid valve*. A fail safe solenoid valve that shuts off flow through the units when an adequate UV dose is not being achieved must be installed. |
| uvDisNSFStndCertN | (SW Treatment) (UV Disinfection <40 gpm) Does this UV unit have an NSF Standard 55A Certification or has it been validated according to the requirements of the 2006 UV Disinfection Guidance Manual? | The system has a potential violation. The UV unit being used by the system for Cryptosporidium inactivation credit does not have the required NSF 55A Certification (less than 40 gpm UV) or validation according to the UVDGM / DVGW (greater than 40 gpm UV). |
| uvDisLT40SensCaliN | (SW Treatment) (UV Disinfection >40 gpm) Is the calibration of the UV intensity sensors checked at least monthly using a reference sensor | The system does not check the calibration of their UV intensity sensors at least monthly. As a system that utilizes UV disinfection to achieve Cryptosporidium inactivation credit to meet the requirements of the Long Term 2 Enhanced Surface Water Treatment Rule, you are required to verify the calibration of all UV sensors monthly and recalibrate the sensors if they do not meet the quality control requirements specified in the EPA UV Disinfection Guidance Manual. The system currently does not conduct UV intensity sensor calibration verifications. The system must work with the UV unit manufacturer to begin performing and documenting monthly UV intensity sensor calibration verifications on all UV units. If any UV sensor does not meet the quality control requirements specified in the UV Disinfection Guidance Manual, it must be recalibrated. |
| uvDisLT40TrnsmCalibN | (SW Treatment) (UV Disinfection >40 gpm) Is the calibration of the UV transmittance analyzer checked at least weekly with a benchtop analyzer (Calculated Dose Method only)? | The system does not check the calibration of their online UV transmittance analyzer on a weekly basis. As a system that utilizes UV disinfection to achieve Cryptosporidium inactivation credit to meet the requirements of the Long Term 2 Enhanced Surface Water Treatment Rule, you are required to continuously monitor the finished water UV transmittance. This parameter is a primary input into the calculated dose equation used to demonstrate that adequate inactivation is being achieved. The system currently does not conduct UV transmittance analyzer calibration verifications. The system must begin conducting weekly verification of the online UVT analyzer using a grab sample. |
| uvDisLT40CalibFlowMN | (SW Treatment) (UV Disinfection >40 gpm) Is there a calibrated flowmeter to ensure max flow rate is not exceeded? | The system currently does not have a calibrated flow meter on one or more of the UV disinfection units*. As a system that utilizes UV disinfection to achieve Cryptosporidium inactivation credit to meet the requirements of the Long Term 2 Enhanced Surface Water Treatment Rule, you are required to monitor the flow rate at each UV unit to ensure that the units are being operated within the validated conditions. Currently, the flow meter at one or more of the UV units is inoperable. The system must repair all flow meters as necessary to allow for direct monitoring of the flow rate at each UV unit. |
| uvdisFTMRecs40N | (SW Treatment) (UV Disinfection >40 gpm) Are daily operational records kept of flow rates/production, run time, lamp status, UV intensity, UVT and UV dosage? | System has a potential violation for failing to maintain UV operation records (greater than 40 gpm UV) (141.720d5). |
| uvDisLT40OperIDEvntN | (SW Treatment) (UV Disinfection >40 gpm) Does the operator know how to identify an off-specification event and report it to the EPA? | The system operators do not know how to properly identify an off-specification event and report it to the EPA (greater than 40 gpm UV). (no standard language) |
| uvDisLT40SysAlarmEvN | (SW Treatment) (UV Disinfection >40 gpm) Does the system alarm when an off-specification event occurs? | The plant's SCADA is not set up to alarm when an off-specification event occurs (greater than 40 gpm UV)*. (no standard language) |
| uvDisFTMPoeRsdN | (SW Treatment) (Chlorination) Is this before the 1st user of the water? | System has a potential violation for monitoring the POE chlorine residual at a point that is not prior to the first user of the water (141.74c2). |
| chmDis2MsmtN | (SW Treatment) (Chlorination) Are the two measurements within 0.1 mg/L or 15% of one another (whichever is larger)? | Inadequate Treatment Process Monitoring for Surface Water Treatment Plants. The online chlorine residual analyzer at the point of entry was not adequately calibrated and periodically verified. The chlorine residual at the point of entry measured by the surveyor using a handheld DPD device varied substantially from the reading by the online analyzer. According to EPA Method 334.0: Determination of Residual Chlorine in Drinking Water Using an On-Line Chlorine Analyzer; during routine calibration checks of the online analyzer, the continuous analyzer chlorine residual reading must be within 0.1 mg/L or 15% (whichever is greater) of the grab sample measurement. If the readings are outside of this range, follow-up calibration procedures are required. The following actions must be taken: a. The online analyzer should be calibrated per manufacturer’s specifications and then checked with a grab sample taken at the same location (using an accurate handheld DPD analyzer) to ensure that the variance is within the specified limits. If after calibration the device still does not meet the above requirements, the system should contact the manufacturer to troubleshoot the problem and calibrate the instrument. b. The online analyzer should be verified with a grab sample once every seven days and records of the verifications kept in the operating logs. If the variance between the two readings is ever outside of the specified limits (0.1 mg/L or 15%, whichever is larger), the online chlorine residual analyzer should be calibrated and re-checked. If this does not bring the readings within the specified limits, the system should contact the manufacturer to troubleshoot the problem. |
| chmDisMeaResidContN | (SW Treatment) (Chlorination) If measuring residual continuously, is the PWS conducting weekly verifications with a grab sample measurement? | Inadequate Treatment Process Monitoring, Recording, and Recordkeeping for Surface Water Treatment Plants. The online chlorine residual analyzer at the point of entry to the distribution system was not periodically verified to determine the need for calibration per the requirements of EPA Method 334.0: Determination of Residual Chlorine in Drinking Water Using an On-Line Chlorine Analyzer. The online analyzer must be verified with a grab sample once every seven days and records of the weekly verifications kept in the operating logs. The continuous analyzer chlorine residual reading must be within 0.1 mg/L or 15% (whichever is greater) of the grab sample measurement. If the readings are outside of this range, follow-up calibration procedures are required. |
| chmDisFTMBromaN | (SW Treatment) (Ozonation) Does the system monitor bromate concentration at point of entry? | System has a potential violation for failing to monitor bromate at the point of entry according to the required frequency (system using ozone) (141.132b3). |
| chmDisFTMClDioxN | (SW Treatment) (Chlorine Dioxide) Does the system monitor chlorine dioxide daily at point of entry? | System has a potential violation for failing to monitor chlorine dioxide at the point of entry according to the required frequency (system using chlorine dioxide) (141.132c2). |
| chmDisFTMChloritN | (SW Treatment) (Chlorine Dioxide) Does the system monitor chlorite at point of entry daily and monthly in the distribution system? | System has a potential violation for failing to monitor chlorite at the point of entry according to the required frequency (system using chlorine dioxide) (141.132b2). |
| chmDis1YrProfNCmN | (SW Treatment) (Disinfection Profiling) Does the system have a disinfection profile on site that contains a year of weekly log inactivation calculations (<10,000 pop.) or a year of daily log inactivation calculations (>10,000 pop)? | One year disinfection profile not completed. This public water system was required to conduct one year of disinfection profiling as part of the Long Term 1 Enhanced Surface Water Treatment Rule. The disinfection profile consists of inactivation calculations for Giardia and viruses calculated once per week over a year’s time. During this sanitary survey, a complete one year profile was not available for review. The system must collect information on the plant’s flow rate, contact tank volume, pH, temperature, and chlorine residual on at least a weekly basis to calculate Giardia and virus inactivation levels for one year. This information should be used to complete the required one year disinfection profile and the profile should then be kept in the plant’s records indefinitely. Failure to have the profile available for review during sanitary surveys is a recordkeeping violation of 40 C.F.R. §141.536. |
| chmDisFTConsultN | (SW Treatment) (Disinfection Profiling) If yes, was the EPA consulted? | System has a potential violation for failing to consult the EPA prior to making a significant change to their disinfection practices (141.570d or 141.172c). |
| virGiVGt4RmvN | (SW Treatment) (Overall Removal Virus) > 4 logs? | Inadequate inactivation design or operation (CT)*. The Surface Water Treatment Rule requires that water systems achieve at least 99.99% (4-log) removal and/or inactivation of viruses. The cartridge filtration system employed is not credited with any virus removal due to the large size of the pores in comparison with the size of viruses. In addition, the UV system is not credited with virus inactivation due to the relatively high UV resistance of viruses. The system must therefore achieve 99.99% inactivation of viruses through chemical disinfection. Based upon calculations made in this sanitary survey using conservative values, the required level of virus inactivation is not achieved by the time the water reaches the first user. The system must ensure adequate inactivation; the disinfection profiling spreadsheet sent to the system should be used weekly for one year to document adequate inactivation. If the system is unable to achieve the required 4 log inactivation by adjusting the flow rate or chlorine residual, it is possible that modifications to the system design will be necessary. |
| virGiGt3RmvN | (SW Treatment) (Overall Removal Giardia) > 3 logs? | Inadequate inactivation design or operation (CT)*. The water treatment system operation and/ or design does not provide for adequate inactivation of Giardia lamblia. The SWTR requires that water systems achieve at least 99.9% (3-log) removal and/or inactivation of Giardia lamblia cysts and 99.99% (4-log) removal and/or inactivation of viruses. As documented in this sanitary survey, the filtration system when properly operated does not achieve the required reduction of Giardia; therefore, the system must achieve additional reduction of Giardia through inactivation. The system does not routinely collect and record the data necessary to determine the level of inactivation. Inactivation calculations made based on data collected during the sanitary survey and standard conservative estimates for peak hourly flows and tank and pipeline volumes indicated that the system was not obtaining enough Giardia inactivation to achieve a total reduction (removal plus inactivation) of 99.9%. The system must ensure adequate Giardia reduction; the disinfection profiling spreadsheet provided to the water system should be used weekly to document that the inactivation necessary to achieve the required total reduction of Giardia is achieved. A completed copy must be provided to EPA to show that this significant deficiency has been resolved. If the system is unable to obtain the required inactivation, the system should be modified to increase the level of inactivation (i.e. installation of a second method of inactivation or installation of additional storage to increase contact time). |
| InCryptoInacN | (SW Treatment) (Overall Removal Cryptosporidium) > required logs? | System has a potential violation for failing to maintain adequate treatment for Cryptosporidium as required in the LT2 rule (Bins 2 or higher system or system that committed to install maximum treatment) (141.711a).* |
| disDat20PSIN | (Distribution) Is there at least 20 psi at all points in the system at all times? | Low pressure or loss of pressure (less than 20 psi)*. Presently, some areas of the distribution system have pressure less than 20 psi. This low pressure creates significant risk for backflow and system contamination. In order to correct this significant deficiency, you must identify the cause(s) of the low pressure and provide documentation of how it was corrected. |
| disDatbulkrpz1N | (Distribution) Bulk Water Supply / Fill Station Appropriate Air Gap or RPZ? | Inadequate backflow prevention on [insert station name] bulk water fill station*. (See photo #) Bulk water fill stations present a potential cross-connection. Cross-connections provide a pathway for contamination to enter the drinking water system during backflow events and therefore present a potential public health threat. A reduced pressure backflow assembly (RPZ) or permanent air gap device must be installed at this facility. An RPZ must be inspected and tested at least annually to ensure proper function. For corrective actions refer to WY DEQ Chapter 12 Section 14(i) regulations on Cross Connections. |
| disDatbulkrpz2N | (Distribution) Bulk Water Supply / Fill Station Appropriate Air Gap or RPZ? | Inadequate backflow prevention on [insert station name] bulk water fill station*. (See photo #) Bulk water fill stations present a potential cross-connection. Cross-connections provide a pathway for contamination to enter the drinking water system during backflow events and therefore present a potential public health threat. A reduced pressure backflow assembly (RPZ) or permanent air gap device must be installed at this facility. An RPZ must be inspected and tested at least annually to ensure proper function. For corrective actions refer to WY DEQ Chapter 12 Section 14(i) regulations on Cross Connections. |
| disDatbulkrpz3N | (Distribution) Bulk Water Supply / Fill Station Appropriate Air Gap or RPZ? | Inadequate backflow prevention on [insert station name] bulk water fill station*. (See photo #) Bulk water fill stations present a potential cross-connection. Cross-connections provide a pathway for contamination to enter the drinking water system during backflow events and therefore present a potential public health threat. A reduced pressure backflow assembly (RPZ) or permanent air gap device must be installed at this facility. An RPZ must be inspected and tested at least annually to ensure proper function. For corrective actions refer to WY DEQ Chapter 12 Section 14(i) regulations on Cross Connections. |
| disDatARVLeakY | (Distribution) Do any (ARVs) have leaks and/or standing water that covers the discharge point? | Air relief valve (ARV) vault contains standing water (see photo #) An ARV vault near [describe location] contained standing water from ground water intrusion or leaks in the pipes or valves. Standing water at the discharge point of the air relief valve could create a potential backflow problem if the system loses pressure and the water is siphoned back into the main. |
| crsConnRedPrsBckN | (Cross Connection Control) Does each severe hazard connection have the appropriate reduced pressure backflow assembly installed at the meter/service connection and approved air gap (twice the size of the supply pipe diameter but always greater than one inch)? | Unprotected, severe hazard cross-connection present*. (See photo #) (see examples listed below) Cross-connections provide a pathway for contamination to enter the drinking water system during backflow events and therefore present a potential public health threat. The survey identified [specify the cross connection found during the survey] as a severe hazard cross connection. A reduced pressure backflow assembly and air gap that is twice the size of the supply pipe diameter but always greater than one inch must be installed at the service connection to this facility and must be inspected and tested at least annually to ensure proper function. For corrective actions refer to WY DEQ Chapter 12 Section 14(i) regulations on Cross Connections. |
| crsConnAirGapN | (Cross Connection Control) Does each high hazard connection in the treatment plant or distribution system have the appropriate air gap or reduced pressure backflow assembly installed? | Unprotected, high hazard cross-connection present*. (See photo #) (see examples listed below) Cross-connections provide a pathway for contamination to enter the drinking water system during backflow events and therefore present a potential public health threat. The survey identified [specify the cross connection found during the survey] as a high hazard cross connection. A reduced pressure backflow assembly (RPZ) or air gap must be installed at the service connection to this facility. An RPZ must be inspected and tested at least annually to ensure proper function. For corrective actions refer to WY DEQ Chapter 12 Section 14(i) regulations on Cross Connections. |
| crsConnLeakCompY | (Cross Connection Control) Were there any leaking system components observed by the surveyor that are not previously noted? | Leaking system components were identified [describe type and location]. [Describe potential concern and remedy] |
| crsConnStckTnkAirGpN | (Cross Connection Control) (non-community systems only) Stock tanks – approved air gap or atmospheric vacuum breaker at the tank? | Unprotected, high hazard cross-connection present*. (See photo #)(see examples listed below) For Noncommunity Systems Only: Stock tanks are high hazard cross connections because of the potential for protozoan, bacterial and viral contamination. An approved air gap or atmospheric vacuum breaker or greater backflow prevention device must be installed at the tank(s). |
| mangDatPropOpN | (Management) Is the treatment plant being properly operated to prevent inadequately treated water from being sent to the distribution system? | The treatment plant is not being operated to prevent inadequately treated water from being sent to the distribution system*. During the sanitary survey the operator demonstrated lack of operational understanding or other limiting conditions existed [describe]. [Describe potential concern and remedy] |

| ALERTS | Rule | Message | Rule manager |
| --- | --- | --- | --- |
| chkChangesWS | Inventory | Have there been any changes to the water system since the last survey? - Yes | Bolor and Donna |
| chkConsPhoBsdInhib1 | LCR | Phosphate based inhibitor used by consecutive system 1 - Yes | Chelsea |
| chkConsPhoBsdInhib2 | LCR | Phosphate based inhibitor used by consecutive system 2 - Yes | Chelsea |
| chkConsSilBsdInhib2 | LCR | Silica based inhibitor used by consecutive system 2 - Yes | Chelsea |
| chkConsPhoBsdInhib3 | LCR | Phosphate based inhibitor used by consecutive system 3 - Yes | Chelsea |
| chkConsSilBsdInhib3 | LCR | Silica based inhibitor used by consecutive system 3 - Yes | Chelsea |
| chkAddChemsCorrCntlY | LCR | System adds corrosion control chemicals to dist system. | Chelsea |
| chkNoLCRSmplSitePlan | LCR | No LCR Tap Sample Site plan on file. | Chelsea |
| chkNoLCRSmplSitePlan | LCR | Operator not following the LCR Tap Sample Site plan. | Chelsea |
| chkAsbBetwnSrcTreat1 | Chem | Is there asbestos pipe in the water system between the source and the treatment plant? - Yes | Kendra |
| chkAsbBetwnSrcTreat2 | Chem | Is there asbestos pipe in the water system between the source and the treatment plant? - Yes | Kendra |
| chkAsbInDistSystem | Chem | Is there asbestos pipe in the distribution system? -Yes | Kendra |
| chkEvaluImpctWeathEv | Water Security | Have you evaluated impacts to water system due to extreme weather events?- Yes | Nara |
| chkIntTrainWeathEvnt | Water Security | Interested in training on weather events preparedness? - Yes | Nara |
| chkKnowEntrPtSmplTp | Nit | Does the operator know the location of each sample tap that represents the entry point(s) to the distribution system? (sample location for Nitrates, RADs, IOCs, SOCs and VOCs) - <No> | Bailey |
| chkOpLabelEntPtSmpl | Nit | Does the operator know how to properly label samples taken from the entry point(s)?- <No> | Bailey |
| WL1SrWTpGWN | GWR | Is there a source water sample tap for GWR compliance? <No> | Jamie |
| WL1TpPriPTN | GWR | Is the tap located prior to all treatment processes? <No> | Jamie |
| WL2SrWTpGWN | GWR | Is there a source water sample tap for GWR compliance? <No> | Jamie |
| WL2TpPriPTN | GWR | Is the tap located prior to all treatment processes? <No> | Jamie |
| WL3SrWTpGWN | GWR | Is there a source water sample tap for GWR compliance? <No> | Jamie |
| WL3TpPriPTN | GWR | Is the tap located prior to all treatment processes? <No> | Jamie |
| WL4SrWTpGWN | GWR | Is there a source water sample tap for GWR compliance? <No> | Jamie |
| WL4TpPriPTN | GWR | Is the tap located prior to all treatment processes? <No> | Jamie |
| WL5SrWTpGWN | GWR | Is there a source water sample tap for GWR compliance? <No> | Jamie |
| WL5TpPriPTN | GWR | Is the tap located prior to all treatment processes? <No> | Jamie |
| WL6SrWTpGWN | GWR | Is there a source water sample tap for GWR compliance? <No> | Jamie |
| WL6TpPriPTN | GWR | Is the tap located prior to all treatment processes? <No> | Jamie |
| sprSrcWTpGWN | GWR | Is there a source water sample tap for GWR compliance? <No> | Jamie |
| sprTpPriPTN | GWR | Is the tap located prior to all treatment processes? <No> | Jamie |
| chkRTCRSmplPlnFileY | RTCR | Does the system have an RTCR sampling plan on file and available for the surveyor’s review (give date of plan)? - Yes | Jamie |
| chkRTCRSmplPlnFileN | RTCR | Does the system have an RTCR sampling plan on file and available for the surveyor’s review (give date of plan)? - No | Jamie |
| chkOpFollowTCRSmplPl | RTCR | Ask the operator - Is the system following their RTCR sampling plan? If No, explain any difficulties | Jamie |
| chkCommunity | DBP | Community water system | Seth |
| chkNonTrNonComm | DBP | Non-Trans Non-Community system | Seth |
| chkHasDBPMonitPlanNo | DBP | Has no DBP Monitoring plan. | Seth |
| chkDBPMonPlnUpToDtNo | DBP | The DBP Monitoring Plan is not up to date, reflecting the current dist system. | Seth |
| chk5YrMainsExtendedY | DBP | The Water mains have been extended to new service areas. | Seth |
| PWSMonCorrCntlPrmsN | LCR | PWS monitor corrosion control treatment chemical concentrations, pH or any other water quality parameters at the entry point | Chelsea |