{"text_format":"3","workbook":"xlsx","n_sheets":8,"sheets":["Notes","Existing Area Source ≤500 HP","Existing Area Source >500 HP","Existing Major Source ≤500 HP","Existing Major Source >500 HP","New&Recon Major Source ≤500 HP","New&Recon Major Source  >500 HP","New & Reconstructed Area Source"],"not_rendered":{"defined_names":14},"read":"whole","date_system":"1900"}

{"sheet":"Notes","index":0,"n_rows":13,"n_cols":2,"rows_kept":13,"merged":[[0,0,1,1]]}
["Please note that each tab is for a different category of engine.  You can either refer to the descriptive header at the top of each page to determine your engine type, or refer to the Applicability Flowchart under \"Implementation Information\" at http://www.epa.gov/ttn/atw/rice/ricepg.html."]
[]
[]
[]
["Date of Revision","Description of Revision"]
["2010-12-03","Table of Requirements was revised to correct the compliance date in cell C18 of STEP 1a for existing stationary engines >500 HP at area sources to 10/19/2013."]
["2011-02-22","Revisions to change tab names.  Under Step 1a, \"Footnote 1 of Table 2d\" corrected to read \"Footnote 2 of Table 2d.\" Compliance date for residential/commercial/institutional emergency engines clarified, as it depends on whether the engine is CI or SI.  The compliance date is 10/19/13 for SI engines and 5/3/13 for CI engines."]
["2012-03-01","Revised to eliminate reference to 40 CFR §63.6625(k)."]
["2012-04-10","Revised cell D1 (column heading) of STEP 1a from \"Emission Limitations\" to \"Emission Limitations/Management Practices.\""]
["2012-04-10","Revised cell D1 (column heading) of STEP 2a from \"Emission Limitations\" to \"Emission Limitations/Work Practices.\""]
["2013-02-19","Revised to reflect current version of 40 CFR part 63, subpart ZZZZ (78 FR 6673) published January 30, 2013."]
["2014-01-09","Revised cells J8 and J12 of STEP 1a to remove reference to §63.6635"]
["2014-02-05","Revised cells L8 and L12 of STEP 1a to indicate that §63.6655(b) does not apply"]

{"sheet":"Existing Area Source ≤500 HP","index":1,"n_rows":29,"n_cols":14,"rows_kept":29,"merged":[[1,0,1,13],[2,0,2,13],[3,0,3,13],[12,3,12,13],[13,3,13,13]]}
["Engine Category","Date Constructed","Compliance Date","Emission Limitations, Management Practices, and Other Requirements","Operating Limitations","Fuel Requirements","Performance Tests","Monitoring, Installation, Collection, Operation and Maintenance Requirements","Initial Compliance","Continuous Compliance","Notification Requirements","Recordkeeping Requirements","Reporting Requirements","General Provisions              (40 CFR part 63)"]
[" Stationary RICE at Area Sources"]
["STEP 1a - Existing Area Sources"]
["Existing Stationary Engine ≤500 HP Located at Area Sources of HAP"]
["Emergency CI","Before 6/12/2006","2013-05-03","63.6603(a), Table 2d","No Requirements",">100 HP, <30 l/cyl  AND >15 hrs/yr for emergency DR: 63.6604(b)","No Requirements","63.6625(e), (f), (h), (i)","No Requirements","63.6605, 63.6640 ","No Requirements","63.6655 (except 63.6655(c))",">100 HP and >15 hrs/yr for emergency DR: 63.6650(h), All engines: Footnote 2 of Table 2d","Yes, except per 63.6645(a)(5), the following do not apply:  63.7(b) and (c), 63.8(e), (f)(4) and (f)(6), and 63.9(b)-(e), (g) and (h)."]
["Non-Emergency CI 300<HP≤500","Before 6/12/2006","2013-05-03","63.6603(a)-(e), Table 2da,b","No Requirements",">300 HP with displacement <30 l/cyl: 63.6604(a)","63.6612, 63.6620, Table 4, Table 5","63.6625(h), ≥300 HP: 63.6625(g)","63.6630, Table 5","63.6605, 63.6640 ",63.6645,"63.6655 (except 63.6655(c) and (f))","63.6650 (except 63.6650(g))","Yes"]
["Non-Emergency CI ≤300 HP ","Before 6/12/2006","2013-05-03","63.6603(a), Table 2d","No Requirements","No Requirements","No Requirements","63.6625(e), (h), (i)                  ","No Requirements","63.6605, 63.6640 ","No Requirements","63.6655 (except 63.6655(c) and (f))","No Requirements","Yes, except per 63.6645(a)(5), the following do not apply:  63.7(b) and (c), 63.8(e), (f)(4) and (f)(6), and 63.9(b)-(e), (g) and (h)."]
["Emergency SI","Before 6/12/2006","2013-10-19","63.6603(a), Table 2d","No Requirements","No Requirements","No Requirements","63.6625(e), (f), (h), (j)     ","No Requirements","63.6605, 63.6640 ","No Requirements","63.6655 (except 63.6655(c))",">100 HP and >15 hrs/yr for emergency DR: 63.6650(h), All engines: Footnote 2 of Table 2d","Yes, except per 63.6645(a)(5), the following do not apply:  63.7(b) and (c), 63.8(e), (f)(4) and (f)(6), and 63.9(b)-(e), (g) and (h)."]
["Non-Emergency SI 4SLB","Before 6/12/2006","2013-10-19","63.6603(a), Table 2d","No Requirements","No Requirements","No Requirements","63.6625(e), (h), (j)     ","No Requirements","63.6605, 63.6640","No Requirements","63.6655 (except 63.6655(c) and (f))","No Requirements","Yes, except per 63.6645(a)(5), the following do not apply:  63.7(b) and (c), 63.8(e), (f)(4) and (f)(6), and 63.9(b)-(e), (g) and (h)."]
["Non-Emergency SI 2SLB","Before 6/12/2006","2013-10-19","63.6603(a), Table 2d","No Requirements","No Requirements","No Requirements","63.6625(e), (h), (j)     ","No Requirements","63.6605, 63.6640","No Requirements","63.6655 (except 63.6655(c) and (f))","No Requirements","Yes, except per 63.6645(a)(5), the following do not apply:  63.7(b) and (c), 63.8(e), (f)(4) and (f)(6), and 63.9(b)-(e), (g) and (h)."]
["Non-Emergency SI 4SRB","Before 6/12/2006","2013-10-19","63.6603(a), Table 2d","No Requirements","No Requirements","No Requirements","63.6625(e), (h), (j)     ","No Requirements","63.6605, 63.6640","No Requirements","63.6655 (except 63.6655(c) and (f))","No Requirements","Yes, except per 63.6645(a)(5), the following do not apply:  63.7(b) and (c), 63.8(e), (f)(4) and (f)(6), and 63.9(b)-(e), (g) and (h)."]
["Non-Emergency Landfill/Digester Gas","Before 6/12/2006","2013-10-19","63.6603(a), Table 2d","No Requirements","No Requirements","No Requirements","63.6625(e), (h), (j)     ","No Requirements","63.6605, 63.6640","No Requirements","63.6655 (except 63.6655(c) and (f))","No Requirements","Yes, except per 63.6645(a)(5), the following do not apply:  63.7(b) and (c), 63.8(e), (f)(4) and (f)(6), and 63.9(b)-(e), (g) and (h)."]
["Residential/Commerical/Institutional Emergency CI","Before 6/12/2006","2013-05-03","These engines are subject to the requirements in 40 CFR 63.6640(f).  No other requirements apply."]
["Residential/Commerical/Institutional Emergency SI","Before 6/12/2006","2013-10-19","These engines are subject to the requirements in 40 CFR 63.6640(f).  No other requirements apply."]
["aNote that engines that meet the conditions in 63.6603(b)(1) or (b)(2) must meet management practices for non-emergency CI engines <300 HP in Table 2d."]
["bNote that an engine located on an offshore vessel and is a nonroad vehicle that is an Outer Continental Shelf (OCS) is subject to management practices specified at 63.6603(c)."]
["cNote that certain engines covered under 40 CFR part 63, subpart ZZZZ, may be subject to additional requirements under 40 CFR part 60, subparts IIII and JJJJ."]
["dFor assistance in determining the potential to emit, please refer to http://www.epa.gov/ttn/chief/ap42/index.html or contact your EPA regional office or state permitting staff.  To determine the potential to emit, you may use emission factors from http://www.epa.gov/ttn/chief/ap42/ch03/index.html, test data, or other published information. "]
["eNote emergency engines have to comply with the definition of an emergency stationary RICE, which includes being operated per the requirements in 40 CFR 63.6640(f).  "]
[]
[]
[]
[]
["Abbreviations:"]
["CI-Compression Ignition"]
["SI-Spark Ignition"]
["4SLB-4 Stroke Lean Burn"]
["2SLB-2 Stroke Lean Burn"]
["4SRB-4 Stroke Rich Burn"]

{"sheet":"Existing Area Source >500 HP","index":2,"n_rows":32,"n_cols":14,"rows_kept":32,"merged":[[1,0,1,13],[2,0,2,13],[3,0,3,13],[15,3,15,13],[16,3,16,13]]}
["Engine Category","Date Constructed","Compliance Date","Emission Limitations, Management Practices, and Other Requirements","Operating Limitations","Fuel Requirements","Performance Tests","Monitoring, Installation, Collection, Operation and Maintenance Requirements","Initial Compliance","Continuous Compliance","Notification Requirements","Recordkeeping Requirements","Reporting Requirements","General Provisions              (40 CFR part 63)"]
[" Stationary RICE at Area Sources"]
["STEP 1a - Existing Area Sources"]
["Existing Stationary Engine >500 HP Located at Area Sources of HAP "]
["Emergency CI","Before 6/12/2006","2013-05-03","63.6603(a), Table 2d","No Requirements",">100 HP, <30 l/cyl  AND >15 hrs/yr for emergency DR: 63.6604(b)","No Requirements","63.6625(e), (f), (h,) (i)","No Requirements","63.6605, 63.6640","No Requirements","63.6655 (except 63.6655(c))",">100 HP and >15 hrs/yr for emergency DR: 63.6650(h), All engines: Footnote 2 of Table 2d","Yes, except per 63.6645(a)(5), the following do not apply:  63.7(b) and (c), 63.8(e), (f)(4) and (f)(6), and 63.9(b)-(e), (g) and (h)."]
["Non-Emergency CI","Before 6/12/2006","2013-05-03","63.6603(a)-(e), Table 2da,b","63.6603, Table 2b",">300 HP with displacement <30 l/cyl: 63.6604(a)","63.6612                   63.6615                    63.6620                      Table 3                      Table 4                      Table 5","63.6625(a), (b), (g), (h)","63.6630                          Table 5","63.6605, 63.6635, 63.6640",63.6645,"63.6655 (except 63.6655(c), (e) and (f))","63.6650                                     (except 63.6650(g))","Yes"]
["Emergency SI","Before 6/12/2006","2013-10-19","63.6603(a), Table 2d","No Requirements","No Requirements","No Requirements","63.6625(e), (f), (h), (j)     ","No Requirements","63.6605, 63.6640","No Requirements","63.6655 (except 63.6655(c))",">100 HP and >15 hrs/yr for emergency DR: 63.6650(h), All engines: Footnote 2 of Table 2d","Yes, except per 63.6645(a)(5), the following do not apply:  63.7(b) and (c), 63.8(e), (f)(4) and (f)(6), and 63.9(b)-(e), (g) and (h)."]
["Non-Emergency SI 4SLB REMOTE                                                                  ","Before 6/12/2006","2013-10-19","63.6603(a), (f), Table 2d","No Requirements","No Requirements","No Requirements","63.6625(e), (h), (j)     ","No Requirements","63.6605, 63.6640","No Requirements","63.6655 (except 63.6655(b), (c) and (f))","No Requirements","Yes"]
["Non-Emergency SI 4SLB NON-REMOTE                   (that operate more than 24 hours per year)","Before 6/12/2006","2013-10-19","63.6603(a), Table 2d","No Requirements","No Requirements","Table 5","63.6625(h)     ","63.6630                          Table 5","63.6605, 63.6635, 63.6640",63.6645,"63.6655 (except 63.6655(c), (e) and (f))","63.6650 (except 63.6650(g))","Yes"]
["               Non-Emergency SI 4SLB                                                (that operate 24 hours or less per year)","Before 6/12/2006","2013-10-19","63.6603(a), Table 2d","No Requirements","No Requirements","No Requirements","63.6625(e), (h), (j)     ","No Requirements","63.6605, 63.6640","No Requirements","63.6655 (except 63.6655(c) and (f))","No Requirements","Yes, except per 63.6645(a)(5), the following do not apply:  63.7(b) and (c), 63.8(e), (f)(4) and (f)(6), and 63.9(b)-(e), (g) and (h)."]
["Non-Emergency SI 2SLB","Before 6/12/2006","2013-10-19","63.6603(a), Table 2d","No Requirements","No Requirements","No Requirements","63.6625(e), (h), (j)     ","No Requirements","63.6605, 63.6640","No Requirements","63.6655 (except 63.6655(c) and (f))","No Requirements","Yes, except per 63.6645(a)(5), the following do not apply:  63.7(b) and (c), 63.8(e), (f)(4) and (f)(6), and 63.9(b)-(e), (g) and (h)."]
["Non-Emergency SI 4SRB REMOTE                                                                  ","Before 6/12/2006","2013-10-19","63.6603(a), (f), Table 2d","No Requirements","No Requirements","No Requirements","63.6625(e), (h), (j)     ","No Requirements","63.6605, 63.6640","No Requirements","63.6655 (except 63.6655(b), (c) and (f))","No Requirements","Yes"]
["Non-Emergency SI 4SRB NON-REMOTE                   (that operate more than 24 hours per year)","Before 6/12/2006","2013-10-19","63.6603(a), Table 2d","No Requirements","No Requirements","Table 5","63.6625(h)","63.6630                          Table 5","63.6605                63.6635                63.6640",63.6645,"63.6655 (except 63.6655(c), (e) and (f))","63.6650                                 (except 63.6650(g))","Yes"]
["            Non-Emergency SI 4SRB                                                (that operate 24 hours or less per year)","Before 6/12/2006","2013-10-19","63.6603(a), Table 2d","No Requirements","No Requirements","No Requirements","63.6625(e), (h), (j)     ","No Requirements","63.6605, 63.6640","No Requirements","63.6655 (except 63.6655(c) and (f))","No Requirements","Yes, except per 63.6645(a)(5), the following do not apply:  63.7(b) and (c), 63.8(e), (f)(4) and (f)(6), and 63.9(b)-(e), (g) and (h)."]
["Non-Emergency Landfill/Digester Gas","Before 6/12/2006","2013-10-19","63.6603(a), Table 2d","No Requirements","No Requirements","No Requirements","63.6625(e), (h), (j)     ","No Requirements","63.6605, 63.6640","No Requirements","63.6655 (except 63.6655(c) and (f))","No Requirements","Yes, except per 63.6645(a)(5), the following do not apply:  63.7(b) and (c), 63.8(e), (f)(4) and (f)(6), and 63.9(b)-(e), (g) and (h)."]
["Residential/Commerical/Institutional Emergency CI","Before 6/12/2006","2013-05-03","These engines are subject to the requirements in 40 CFR 63.6640(f).  No other requirements apply."]
["Residential/Commerical/Institutional Emergency SI","Before 6/12/2006","2013-10-19","These engines are subject to the requirements in 40 CFR 63.6640(f).  No other requirements apply."]
["aNote that engines that meet the conditions in 63.6603(b)(1) or (b)(2) must meet management practices for non-emergency CI engines <300 HP in Table 2d."]
["bNote that an engine located on an offshore vessel and is a nonroad vehicle that is an Outer Continental Shelf (OCS) is subject to management practices specified at 63.6603(c)."]
["cNote that certain engines covered under 40 CFR part 63, subpart ZZZZ, may be subject to additional requirements under 40 CFR part 60, subparts IIII and JJJJ."]
["dFor assistance in determining the potential to emit, please refer to http://www.epa.gov/ttn/chief/ap42/index.html or contact your EPA regional office or state permitting staff.  To determine the potential to emit, you may use emission factors from http://www.epa.gov/ttn/chief/ap42/ch03/index.html, test data, or other published information. "]
["eNote emergency engines have to comply with the definition of an emergency stationary RICE, which includes being operated per the requirements in 40 CFR 63.6640(f).  "]
[]
[]
[]
[]
["Abbreviations:"]
["CI-Compression Ignition"]
["SI-Spark Ignition"]
["4SLB-4 Stroke Lean Burn"]
["2SLB-2 Stroke Lean Burn"]
["4SRB-4 Stroke Rich Burn"]

{"sheet":"Existing Major Source ≤500 HP","index":3,"n_rows":26,"n_cols":14,"rows_kept":26,"merged":[[1,0,1,13],[2,0,2,13],[3,0,3,13]]}
["Engine Category","Date Constructed","Compliance Date","Emission Limitations and Other Requirements","Operating Limitations","Fuel Requirements","Performance Tests","Monitoring, Installation, Collection, Operation and Maintenance Requirements","Initial Compliance","Continuous Compliance","Notification Requirements","Recordkeeping Requirements","Reporting Requirements","General Provisions               (40 CFR part 63)"]
[" Stationary RICE at Major Sources"]
["STEP 2(a)(i)"]
["Existing Stationary Engine ≤500 HP Located at Major Source of HAP "]
["Emergency CI","Before 6/12/2006","2013-05-03","63.6602, Table 2c","No Requirements",">100 HP, <30 l/cyl  AND >15 hrs/yr for emergency DR: 63.6604(b)","No Requirements","63.6625(e), (f), (h), (i)","No Requirements","63.6605, 63.6640","No Requirements","63.6655 (except 63.6655(c))"," >100 HP and >15 hrs/yr for emergency DR: 63.6650(h), All Engines: Footnote 1 of Table 2c","Yes, except per 63.6645(a)(5), the following do not apply:  63.7(b) and (c), 63.8(e), (f)(4) and (f)(6), and 63.9(b)-(e), (g) and (h)."]
["Non-Emergency CI 100≤HP≤500","Before 6/12/2006","2013-05-03","63.6602, Table 2c","No Requirements",">300 HP with displacement <30 l/cyl: 63.6604(a)","63.6612, 63.6620, Table 4, Table 5","≥300 HP: 63.6625(g), All Engines: 63.6625(h)    ","63.6630, Table 5","63.6605, 63.6640",63.6645,"63.6655 (except 63.6655(c), (e), and (f))","63.6650 (except 63.6650(g))","Yes"]
["Non-Emergency CI <100 HP","Before 6/12/2006","2013-05-03","63.6602, Table 2c","No Requirements","No Requirements","No Requirements","63.6625 (e), (h), (i)             ","No Requirements","63.6605, 63.6640","No Requirements","63.6655 (except 63.6655(c) and (f))","No Requirements","Yes, except per 63.6645(a)(5), the following do not apply:  63.7(b) and (c), 63.8(e), (f)(4) and (f)(6), and 63.9(b)-(e), (g) and (h)."]
["Emergency SI","Before 6/12/2006","2013-10-19","63.6602, Table 2c","No Requirements","No Requirements","No Requirements","63.6625(e), (f), (h), (j)     ","No Requirements","63.6605, 63.6640","No Requirements","63.6655 (except 63.6655(c))"," >100 HP and >15 hrs/yr for emergency DR: 63.6650(h), All Engines: Footnote 1 of Table 2c","Yes, except per 63.6645(a)(5), the following do not apply:  63.7(b) and (c), 63.8(e), (f)(4) and (f)(6), and 63.9(b)-(e), (g) and (h)."]
["Non-Emergency SI 4SLB 100≤HP≤500","Before 6/12/2006","2013-10-19","63.6602, Table 2c","No Requirements","No Requirements","63.6612, 63.6620, Table 4, Table 5","63.6625(h)","63.6630, Table 5","63.6605, 63.6640",63.6645,"63.6655 (except 63.6655(c), (e), and (f))","63.6650 (except 63.6650(g))","Yes"]
["Non-Emergency SI 4SLB <100 HP","Before 6/12/2006","2013-10-19","63.6602, Table 2c","No Requirements","No Requirements","No Requirements","63.6625(e), (h), (j)     ","No Requirements","63.6605, 63.6640","No Requirements","63.6655 (except 63.6655(c) and (f))","No Requirements","Yes, except per 63.6645(a)(5), the following do not apply:  63.7(b) and (c), 63.8(e), (f)(4) and (f)(6), and 63.9(b)-(e), (g) and (h)."]
["Non-Emergency SI 2SLB 100≤HP≤500","Before 6/12/2006","2013-10-19","63.6602, Table 2c","No Requirements","No Requirements","63.6612, 63.6620, Table 4, Table 5","63.6625(h)","63.6630, Table 5","63.6605, 63.6640",63.6645,"63.6655 (except 63.6655(c), (e), and (f))","63.6650 (except 63.6650(g))","Yes"]
["Non-Emergency SI 2SLB <100 HP","Before 6/12/2006","2013-10-19","63.6602, Table 2c","No Requirements","No Requirements","No Requirements","63.6625(e), (h), (j)     ","No Requirements","63.6605, 63.6640","No Requirements","63.6655 (except 63.6655(c) and (f))","No Requirements","Yes, except per 63.6645(a)(5), the following do not apply:  63.7(b) and (c), 63.8(e), (f)(4) and (f)(6), and 63.9(b)-(e), (g) and (h)."]
["Non-Emergency SI 4SRB 100≤HP≤500","Before 6/12/2006","2013-10-19","63.6602, Table 2c","No Requirements","No Requirements","63.6612, 63.6620, Table 4, Table 5","63.6625(h)","63.6630, Table 5","63.6605, 63.6640",63.6645,"63.6655 (except 63.6655(c), (e), and (f))","63.6650 (except 63.6650(g))","Yes"]
["Non-Emergency SI 4SRB <100 HP","Before 6/12/2006","2013-10-19","63.6602, Table 2c","No Requirements","No Requirements","No Requirements","63.6625(e), (h), (j)     ","No Requirements","63.6605, 63.6640","No Requirements","63.6655 (except 63.6655(c) and (f))","No Requirements","Yes, except per 63.6645(a)(5), the following do not apply:  63.7(b) and (c), 63.8(e), (f)(4) and (f)(6), and 63.9(b)-(e), (g) and (h)."]
["Non-Emergency Landfill/Digester Gas 100≤HP≤500","Before 6/12/2006","2013-10-19","63.6602, Table 2c","No Requirements","No Requirements","63.6612, 63.6620, Table 4, Table 5","63.6625(h) ","63.6630, Table 5","63.6605, 63.6640",63.6645,"63.6655 (except 63.6655(c), (e), and (f))","63.6650 (except 63.6650(g))","Yes"]
["Non-Emergency Landfill/Digester Gas <100 HP","Before 6/12/2006","2013-10-19","63.6602, Table 2c","No Requirements","No Requirements","No Requirements","63.6625(e), (h), (j)     ","No Requirements","63.6605, 63.6640","No Requirements","63.6655 (except 63.6655(c) and (f))","No Requirements","Yes, except per 63.6645(a)(5), the following do not apply:  63.7(b) and (c), 63.8(e), (f)(4) and (f)(6), and 63.9(b)-(e), (g) and (h)."]
["aNote that certain engines covered under 40 CFR part 63, subpart ZZZZ, may be subject to additional requirements under 40 CFR part 60, subparts IIII and JJJJ."]
["bFor assistance in determining the potential to emit, please refer to http://www.epa.gov/ttn/chief/ap42/index.html or contact your EPA regional office or state permitting staff.  To determine the potential to emit, you may use emission factors from http://www.epa.gov/ttn/chief/ap42/ch03/index.html, test data, or other published information. "]
["cNote emergency engines have to comply with the definition of an emergency stationary RICE, which includes being operated per the requirements in 40 CFR 63.6640(f).  "]
[]
["Abbreviations:"]
["CI-Compression Ignition"]
["SI-Spark Ignition"]
["4SLB-4 Stroke Lean Burn"]
["2SLB-2 Stroke Lean Burn"]
["4SRB-4 Stroke Rich Burn"]

{"sheet":"Existing Major Source >500 HP","index":4,"n_rows":21,"n_cols":14,"rows_kept":21,"merged":[[1,0,1,13],[2,0,2,13],[3,0,3,13],[4,2,4,13],[5,3,5,4],[5,6,5,8],[5,10,5,11],[7,3,7,13],[8,3,8,13],[10,2,10,13]]}
["Engine Category","Date Constructed","Compliance Date","Emission Limitations and Other Requirements","Operating Limitations","Fuel Requirements","Performance Tests","Monitoring, Installation, Collection, Operation and Maintenance Requirements","Initial Compliance","Continuous Compliance","Notification Requirements","Recordkeeping Requirements","Reporting Requirements","General Provisions               (40 CFR part 63)"]
[" Stationary RICE at Major Sources"]
["STEP 2(a)(ii)"]
["Existing Stationary Engine >500 HP Located at Major Source of HAP"]
["Limited Use","Before 12/19/2002","No Requirements"]
["Emergency","Before 12/19/2002","2007-06-15","No Requirements",null,"<30 l/cyl  AND >15 hrs/yr for emergency DR: 63.6604(b)","No Requirements",null,null,"63.6640","No Requirements",null," >100 HP and >15 hrs/yr for emergency DR: 63.6650(h), All Engines: Footnote 1 of Table 2c","No Requirements"]
["Non-Emergency CI","Before 12/19/2002","2013-05-03","63.6600(d), Table 2c","63.6600(d), Table 2b",">300 HP and <30 l/cyl: 63.6604(a)","63.6610, 63.6615, 63.6620, Table 3, Table 4,Table 5","63.6625(a), (b), (g), (h)","63.6630, Table 5","63.6605, 63.6635, 63.6640",63.6645,"63.6655 (except 63.6655(c), (e), and (f))","63.6650 (except 63.6650(g))","Yes"]
["Non-Emergency SI 4SLB","Before 12/19/2002","2007-06-15","No Requirements"]
["Non-Emergency SI 2SLB","Before 12/19/2002","2007-06-15","No Requirements"]
["Non-Emergency SI 4SRB","Before 12/19/2002","2007-06-15","63.6600(a), Table 1a","63.6600(a), Table 1b","No Requirements","63.6610, 63.6615, 63.6620, Table 3, Table 4,Table 5","63.6625(a), (b), (h)","63.6630, Table 5","63.6605, 63.6635, 63.6640",63.6645,"63.6655 (except 63.6655(c), (e), and (f))","63.6650 (except 63.6650(g))","Yes"]
["Landfill/Digester Gas","Before 12/19/2002","No Requirements"]
["aNote that certain engines covered under 40 CFR part 63, subpart ZZZZ, may be subject to additional requirements under 40 CFR part 60, subparts IIII and JJJJ."]
["bFor assistance in determining the potential to emit, please refer to http://www.epa.gov/ttn/chief/ap42/index.html or contact your EPA regional office or state permitting staff.  To determine the potential to emit, you may use emission factors from http://www.epa.gov/ttn/chief/ap42/ch03/index.html, test data, or other published information. "]
["cNote emergency engines have to comply with the definition of an emergency stationary RICE, which includes being operated per the requirements in 40 CFR 63.6640(f).  "]
[]
["Abbreviations:"]
["CI-Compression Ignition"]
["SI-Spark Ignition"]
["4SLB-4 Stroke Lean Burn"]
["2SLB-2 Stroke Lean Burn"]
["4SRB-4 Stroke Rich Burn"]

{"sheet":"New&Recon Major Source ≤500 HP","index":5,"n_rows":24,"n_cols":14,"rows_kept":24,"merged":[[1,0,1,13],[2,0,2,13],[3,0,3,13],[4,2,4,13],[5,2,5,13],[6,2,6,13],[7,2,7,13],[8,2,8,13],[11,2,11,13],[12,2,12,13],[13,2,13,13]]}
["Engine Category","Date Constructed","Compliance Date","Emission Limitations","Operating Limitations","Fuel Requirements","Performance Tests","Monitoring, Installation, Collection, Operation and Maintenance Requirements","Initial Compliance","Continuous Compliance","Notification Requirements","Recordkeeping Requirements","Reporting Requirements","General Provisions (40 CFR part 63)"]
[" Stationary RICE at Major Sources"]
["STEP 2(b)(i)"]
["New & Reconstructed Stationary Engine ≤500 HP Located at Major Source of HAP "]
["Limited Use","On or After 6/12/2006","Engines are subject to 40 CFR part 60, subpart IIII (CI NSPS) or subpart JJJJ (SI NSPS), as applicable."]
["Emergency","On or After 6/12/2006","Engines are subject to 40 CFR part 60, subpart IIII (CI NSPS) or subpart JJJJ (SI NSPS), as applicable."]
["Non-Emergency CI"," On or After 6/12/06","Engines are subject to 40 CFR part 60, subpart IIII (CI NSPS) "]
["SI 4SLB <250 HP","On or After 6/12/2006","Engines are subject to 40 CFR part 60, subpart JJJJ (SI NSPS)"]
["Non-Emergency SI 4SLB ≥250 HP","On or After 6/12/2006 and before 1/1/2008","No Requirements"]
["Non-Emergency SI 4SLB ≥250 HP","Manufactured on or after 1/1/2008","Upon Startup","63.6601, Table 2a","63.6601, Table 2b","No Requirements","63.6611, 63.6615, 63.6620, Table 3, Table 4, Table 5","63.6625(h)","63.6630, Table 5","63.6605, 63.6635, 63.6640",63.6645,"63.6655 (except 63.6655(c), (e), and (f))","63.6650 (except 63.6650 (g))","Yes"]
["Emergency SI 4SLB ≥250 HP","Manufactured on or after 1/1/2008","Upon Startup","No Requirements","No Requirements","No Requirements","No Requirements","63.6625(d), (h)","No Requirements","63.6605, 63.6640","No Requirements","No Requirements","No Requirements","Yes"]
["SI 2SLB","On or After 6/12/2006","Engines are subject to 40 CFR part 60, subpart JJJJ (SI NSPS)"]
["SI 4SRB","On or After 6/12/2006","Engines are subject to 40 CFR part 60, subpart JJJJ (SI NSPS)"]
["Landfill/Digester Gas","On or After 6/12/2006","Engines are subject to 40 CFR part 60, subpart JJJJ (SI NSPS)"]
["aNote that certain engines covered under 40 CFR part 63, subpart ZZZZ, may be subject to additional requirements under 40 CFR part 60, subparts IIII and JJJJ."]
["bFor assistance in determining the potential to emit, please refer to http://www.epa.gov/ttn/chief/ap42/index.html or contact your EPA regional office or state permitting staff.  To determine the potential to emit, you may use emission factors from http://www.epa.gov/ttn/chief/ap42/ch03/index.html, test data, or other published information. "]
["cNote emergency engines have to comply with the definition of an emergency stationary RICE, which includes being operated per the requirements in 40 CFR 63.6640(f).  "]
[]
["Abbreviations:"]
["CI-Compression Ignition"]
["SI-Spark Ignition"]
["4SLB-4 Stroke Lean Burn"]
["2SLB-2 Stroke Lean Burn"]
["4SRB-4 Stroke Rich Burn"]

{"sheet":"New&Recon Major Source  >500 HP","index":6,"n_rows":21,"n_cols":14,"rows_kept":21,"merged":[[1,0,1,13],[2,0,2,13],[3,0,3,13]]}
["Engine Category","Date Constructed","Compliance Date","Emission Limitations","Operating Limitations","Fuel Requirements","Performance Tests","Monitoring, Installation, Collection, Operation and Maintenance Requirements","Initial Compliance","Continuous Compliance","Notification Requirements","Recordkeeping Requirements","Reporting Requirements","General Provisions (40 CFR part 63)"]
[" Stationary RICE at Major Sources"]
["STEP 2(b)(ii)"]
["New & Reconstructed Stationary Engine >500 HP Located at Major Source of HAP"]
["Limited Use","On or After 12/19/2002","Upon Startup","No Requirements","No Requirements","No Requirements","No Requirements","No Requirements","No Requirements",63.6605,"63.6645(f)","No Requirements","No Requirements","No (except as specified in 63.6645(f))"]
["Emergency ","On or After 12/19/2002","Upon Startup","No Requirements","No Requirements","<30 l/cyl  AND >15 hrs/yr for emergency DR:  63.6604(c)","No Requirements","No Requirements","No Requirements","63.6605, 63.6640","63.6645(f)","No Requirements",">15 hrs/yr for emergency DR: 63.6650(h)","No (except as specified in 63.6645(f))"]
["Non-Emergency CI ","On or After 12/19/2002","Upon Startup","63.6600(b), Table 2a","63.6600(b), Table 2b","No Requirements","63.6610, 63.6615, 63.6620, Table 3, Table 4, Table 5","63.6625(a), (b), (h)","63.6630, Table 5","63.6605, 63.6635, 63.6640",63.6645,"63.6655 (except 63.6655(c), (e), and (f))","63.6650, except 63.6650 (g))","Yes"]
["Non-Emergency SI 4SLB","On or After 12/19/2002","Upon Startup","63.6600(b), Table 2a","63.6600(b), Table 2b","No Requirements","63.6610, 63.6615, 63.6620, Table 3, Table 4, Table 5","63.6625(a), (b), (h)","63.6630, Table 5","63.6605, 63.6635, 63.6640",63.6645,"63.6655 (except 63.6655(c), (e), and (f))","63.6650, except 63.6650 (g))","Yes"]
["Non-Emergency SI 2SLB","On or After 12/19/2002","Upon Startup","63.6600(b), Table 2a","63.6600(b), Table 2b","No Requirements","63.6610, 63.6615, 63.6620, Table 3, Table 4, Table 5","63.6625(a), (b), (h)","63.6630, Table 5","63.6605, 63.6635, 63.6640",63.6645,"63.6655 (except 63.6655(c), (e), and (f))","63.6650, except 63.6650 (g))","Yes"]
["Non-Emergency SI 4SRB","On or After 12/19/2002","Upon Startup","63.6600(a), Table 1a","63.6600(a),Table 1b","No Requirements","63.6610, 63.6615, 63.6620, Table 3, Table 4, Table 5","63.6625(a), (b), (h)","63.6630, Table 5","63.6605, 63.6635, 63.6640",63.6645,"63.6655 (except 63.6655(c), (e), and (f))","63.6650, except 63.6650 (g))","Yes"]
["Landfill/Digester Gas","On or After 12/19/2002","Upon Startup","No Requirements","No Requirements","No Requirements","No Requirements","≥10 percent of the gross heat input on an annual basis: 63.6625(c), (h)","No Requirements",63.6605,"≥10 percent of the gross heat input on an annual basis: 63.6645(f)","≥10 percent of the gross heat input on an annual basis: 63.6655(c)","≥10 percent of the gross heat input on an annual basis: 63.6650(g)","No (except as specified in 63.6645(f))"]
["aNote that certain engines covered under 40 CFR part 63, subpart ZZZZ, may be subject to additional requirements under 40 CFR part 60, subparts IIII and JJJJ."]
["bFor assistance in determining the potential to emit, please refer to http://www.epa.gov/ttn/chief/ap42/index.html or contact your EPA regional office or state permitting staff.  To determine the potential to emit, you may use emission factors from http://www.epa.gov/ttn/chief/ap42/ch03/index.html, test data, or other published information. "]
["cNote emergency engines have to comply with the definition of an emergency stationary RICE, which includes being operated per the requirements in 40 CFR 63.6640(f).  "]
[]
["Abbreviations:"]
["CI-Compression Ignition"]
["SI-Spark Ignition"]
["4SLB-4 Stroke Lean Burn"]
["2SLB-2 Stroke Lean Burn"]
["4SRB-4 Stroke Rich Burn"]

{"sheet":"New & Reconstructed Area Source","index":7,"n_rows":29,"n_cols":3,"rows_kept":29,"merged":[[0,2,0,12],[1,0,1,12],[2,0,2,12],[3,0,3,12],[4,2,4,12],[5,2,5,12],[6,2,6,12],[7,2,7,12],[8,2,8,12],[9,2,9,12],[10,2,10,12],[11,0,11,12],[12,2,12,12],[13,2,13,12],[14,2,14,12],[15,2,15,12],[16,2,16,12],[17,2,17,12],[18,2,18,12],[20,0,20,9]]}
["Engine Category","Date Constructed","Requirements"]
[" Stationary RICE at Area Sources"]
["STEP 1b - New & Reconstructed Area Sources"]
["New & Reconstructed Stationary Engine ≤500 HP Located at Area Source of HAP "]
["Limited Use","On or After 6/12/2006","Engines are subject to 40 CFR part 60, subpart IIII (CI NSPS) or subpart JJJJ (SI NSPS), as applicable."]
["Emergency","On or After 6/12/2006","Engines are subject to 40 CFR part 60, subpart IIII (CI NSPS) or subpart JJJJ (SI NSPS), as applicable."]
["Non-Emergency CI","On or After 6/12/2006","Engines are subject to 40 CFR part 60, subpart IIII (CI NSPS) "]
["SI 4SLB","On or After 6/12/2006","Engines are subject to 40 CFR part 60, subpart JJJJ (SI NSPS)"]
["SI 2SLB","On or After 6/12/2006","Engines are subject to 40 CFR part 60, subpart JJJJ (SI NSPS)"]
["SI 4SRB","On or After 6/12/2006","Engines are subject to 40 CFR part 60, subpart JJJJ (SI NSPS)"]
["Landfill/Digester Gas","On or After 6/12/2006","Engines are subject to 40 CFR part 60, subpart JJJJ (SI NSPS)"]
["New & Reconstructed Stationary Engine >500 HP Located at Area Source of HAP"]
["Limited Use","On or After 6/12/2006","Engines are subject to 40 CFR part 60, subpart IIII (CI NSPS) or subpart JJJJ (SI NSPS), as applicable."]
["Emergency","On or After 6/12/2006","Engines are subject to 40 CFR part 60, subpart IIII (CI NSPS) or subpart JJJJ (SI NSPS), as applicable."]
["Non-Emergency CI","On or After 6/12/2006","Engines are subject to 40 CFR part 60, subpart IIII (CI NSPS) "]
["SI 4SLB","On or After 6/12/2006","Engines are subject to 40 CFR part 60, subpart JJJJ (SI NSPS)"]
["SI 2SLB","On or After 6/12/2006","Engines are subject to 40 CFR part 60, subpart JJJJ (SI NSPS)"]
["SI 4SRB","On or After 6/12/2006","Engines are subject to 40 CFR part 60, subpart JJJJ (SI NSPS)"]
["Landfill/Digester Gas","On or After 6/12/2006","Engines are subject to 40 CFR part 60, subpart JJJJ (SI NSPS)"]
["aNote that certain engines covered under 40 CFR part 63, subpart ZZZZ, may be subject to additional requirements under 40 CFR part 60, subparts IIII and JJJJ."]
["bFor assistance in determining the potential to emit, please refer to http://www.epa.gov/ttn/chief/ap42/index.html or contact your EPA regional office or state permitting staff.  To determine the potential to emit, you may use emission factors from http://www.epa.gov/ttn/chief/ap42/ch03/index.html, test data, or other published information. "]
[]
[]
["Abbreviations:"]
["CI-Compression Ignition"]
["SI-Spark Ignition"]
["4SLB-4 Stroke Lean Burn"]
["2SLB-2 Stroke Lean Burn"]
["4SRB-4 Stroke Rich Burn"]