## notes
Notes for example results:
1. All costs are 2016$; Capital Costs include Owners Costs and AFUDC
2. Capital Charge Rate = 14.3% (avg of utility and merchant owned at 15-yr book life)
3. VOM Cost includes Aux Power at $60/MWh and waste disposal at various $/ton rates

## ACI
Fill in the yellow cells with the known data inputs. The resulting costs are tabulated below. Variable names are defined as outlined in the table.
|  |  | Variable |  | Designation | Units | Value | Calculation
|  |  | EPC Project? |  |  |  | FALSE
|  |  | Capacity Factor |  |  |  | 85 | <--- User Input
|  |  | Unit Size |  | A | (MW) | 500 | <--- User Input
|  |  | Retrofit Factor |  | B |  | 1 | <--- User Input (An "average" retrofit has a factor = 1.0)
|  |  | Heat Rate |  | C | (Btu/kWh) | 9500 | <--- User Input
|  |  | Type of Coal |  | D |  | 3 | <--- User Input
|  |  | Existing FGD System |  | E |  | 2 | <--- User Input
|  |  | Existing SCR |  | F |  | TRUE | <--- User Input (Sorbent injection may not be required. Co-benefit of SCR and FGD system should achieve 80% removal.)
|  |  | Removal Less than 80% |  | G |  | FALSE | <--- User Input
|  |  | Existing PM Control |  | H |  | 2 | <--- User Input
|  |  | Baghouse Addition |  | J |  | 1 | <--- User Input for retrofit of an additional baghouse after the existing PM control
|  |  | Type of Sorbent |  | Y |  | 1 | <--- User Input
|  |  | Heat Input |  | K | (Btu/hr) | 4750000000 | A*C*1000
|  |  | Flue Gas Rate |  | L | (acfm) | 1719500 | Downstream of an air preheater For Bituminous Coal = A*C*0.362 For PRB Coal = A*C*0.400 For Lignite Coal = A*C*0.435
|  |  | Sorbent Feed Rate |  | M | (lb/hr) | 515.85 | = If Existing FGD, SCR, and if mercury removal is less than 80% then 0 else L*60/1000000* 2 lb/MMacf for baghouse applications with carbon * 3.5 lb/MMacf for baghouse applications with non-carbn sorbent * 5 lb/MMacf for ESP applications with carbon Not applicable for ESP applications with non-carbn sorbent (Flow determined downstream of an air preheater)
|  |  | Sorbent Waste Rate |  | N | (lb/hr) | 515.85 | =M
|  |  | Fly Ash Waste Rate |  | P | (ton/hr) | 20.7273 | (A*C)* Ash in Coal*(1-Boiler Ash Removal)/(2*HHV) For Bituminous Coal: Ash in Coal = 0.12; Boiler Ash Removal = 0.2; HHV = 11000 For PRB Coal: Ash in Coal = 0.06; Boiler Ash Removal = 0.2; HHV = 8400 For Lignite Coal: Ash in Coal = 0.08; Boiler Ash Removal = 0.2; HHV = 7200
|  |  | Total Waste Rate |  | Q | (ton/hr) | 20.9852 | Based on no beneficial uses for fly ash with activated carbon without an additional baghouse. The use of a the non-carbon sorbent should maintain the current fly ash disposal method. Therefore, only the sorbent waste rate is included for the non-carbon sorbent. if (J = True or G = True or Non-carbon sorbent then 0 else P) + N/2000
|  |  | Aux Power Include in VOM? |  | R | (%) | 0.02 | J= True, then 0.6, else 0 + (0.02)
|  |  | Sorbent Cost - Delivered |  | S | ($/ton) | 1700 | <--- User Input (Standard PAC = $1700, Halogenated PAC = $2100, Non-Carbon Sorbent = $2500)
|  |  | Waste Disposal Cost |  | T | ($/ton) | 30 | <--- User Input
|  |  | Aux Power Cost |  | U | ($/kWh) | 0.06 | <--- User Input
|  |  | Bag Cost |  | V | ($/bag) | 100 | <--- User Input
|  |  | Cage Cost |  | W | ($/cage) | 30 | <--- User Input
|  |  | Operating Labor Rate |  | X | ($/hr) | 60 | <--- User Input (Labor cost including all benefits)
Costs are all based on 2016 dollars
Capital Cost Calcuation | [7 empty] | Example | Comments
Includes - Equipment, intallation, buildings, foundations, electrical, and retrofit difficulty.
| BMC($) = | 1600000*B*(M^0.15) | [5 empty] | 4083000 | Base sorbent injection module includes all equipment from unloading to injection
| BMB ($) = | if (J = Not Added then 0, J = 6.0 Air-to-Cloth then 530, J = 4.0 Air-to-Cloth then 600) *B*L^0.81 | [5 empty] | 0 | Base module for an additional PJFF including: Duct work modifications and reinforcement, foundations, structural steel, ID or booster fans, piping, electrical, etc…
| BMF ($) = | if there is a wet FGD, SCR, and capture is less than 80% then $500,000 else 0 | [5 empty] | 0 | Base module for wet FGD additive addition (as applicable)
| BMA ($) = | if there is an FGD, SCR, the coal is PRB or Lignite, and capture is less than 80% or the coal is PRB or Lignite and the sorbent is standard PAC then $1,000,000 else 0 | [5 empty] | 0 | Base module for coal additive addition (as applicable)
| BM ($) = | BMC+BMB + BMF +BMA | [5 empty] | 4083000 | Total Base module cost including retrofit factor
| BM ($/kW) = | [6 empty] | 8.166 | Base module cost per kW
Total Project Cost
| A1 = 10% of BM | [6 empty] | 408000 | Engineering and Construction Management costs
| A2= if baghouse addition, then 10%, else 5% of BM | [6 empty] | 204000 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc…
| A3 = if baghouse addition, then 10%, else 5% of BM | [6 empty] | 204000 | Contractor profit and fees
| CECC ($) = BM + A1 + A2 + A3 | [6 empty] | 4899000 | Capital, engineering and construction cost subtotal
| CECC ($/kW) = Excludes Owner's Costs = | [6 empty] | 9.798 | Capital, engineering and construction cost subtotal per kW
| B1 = 2% of CECC if EPC TRUE, else 5% of CECC | [6 empty] | 245000 | Owners costs including all "home office" costs (owners engineering, management, and procuement activities)
| B2 = if baghouse addition then 6%, else 0% of CECC +B1 | [6 empty] | 0 | AFUDC: For ACI systems only : 0% for less than 1 year engineering and construction cycle. For additional baghouse: 6% for a 2 year engineering and construction cycle.
| C1 = if EPC = TRUE, 15% of (CECC+B1), else 0 | [6 empty] | 0 | EPC fees of 15%
| C2 = if there is an FGD, SCR, the coal is PRB or Lignite, and capture is less than 80% or the coal is PRB or Lignite and the sorbent in standard PAC then 2500*A else 0 | [6 empty] | 0 | One time coal additive royalty fee (as applicable)
| TPC ($) = Includes Owner's Costs and AFUDC = CECC + B1 + B2 + C1 + C2 | [6 empty] | 5144000 | Total project cost
| TPC ($/kW) = Includes Owner's Costs and AFUDC | [6 empty] | 10.288 | Total project cost per kW
Fixed O&M Cost
| FOMO ($/kW yr) = (0 additional operators)*2080*X/(A*1000) | [6 empty] | 0 | Fixed O&M additional operating labor costs
| FOMM ($/kW yr) =(BM/(B*A*1000)*(0.01 for a sorbent system only or 0.005 when a baghouse is added) | [6 empty] | 0.082 | Fixed O&M additional maintenance material and labor costs
| FOMA ($/kW yr) = 0.03*(FOMO + 0.4*FOMM) | [6 empty] | 0.001 | Fixed O&M additional administrative labor costs
| FOM ($/kW yr) = FOMO +FOMM+FOMA | [6 empty] | 0.083 | Total Fixed O&M costs
Variable O&M Cost
| VOMR ($/MWh) = M*S/(2000*A) | [6 empty] | 0.877 | Variable O&M costs for sorbent
| VOMW ($/MWh) = Q*T/A | [6 empty] | 1.259 | Variable O&M costs for waste disposal that includes both the sorbent and the fly ash waste as applicable
| VOMP ($/MWh) = U*R*10 | [6 empty] | 0.012 | Variable O&M costs for additional auxiliary power required
| VOMB ($/MWh) = if a baghouse is added then L/(J*A*341640)* if(E = 6.0 Air-to-Cloth then (V/3+W/9) else E = 4.0 Air-to-Cloth then (V/5+W/10)) | [6 empty] | 0 | Variable O&M costs for bags and cages.
| VOMF ($/MWh) = if there is a wet FGD, SCR, and capture is less then 80%, then 230/A else 0 | [6 empty] | 0 | Variable O&M costs for wet FGD additive addition
| VOMA ($/MWh) = if there is an FGD, SCR, the coal is PRB or Lignite, and capture is less than 80% or the coal is PRB or Lignite and the sorbent is standard PAC then 0.0298*C/1000 else 0 | [6 empty] | 0 | Variable O&M costs for coal additive addition
| VOM ($/MWh) = VOMR + VOMW + VOMB + VOMP + VOMF + VOMA | [6 empty] | 2.148 | Total Variable O&M costs
[5 empty] | Annual Capacity Factor = | 85%
[5 empty] | Annual MWhs = | 3723000
[5 empty] | Annual Heat Input MMBtu = | 35368500
[5 empty] | Annual lbs Hg in Coal = | n/a
[5 empty] | Annual lbs Hg Removed = | n/a
[5 empty] | Annual lbs Hg Emission = | n/a
[5 empty] | Annual Avg Hg Emission Rate, lb/MMBtu = | n/a
[5 empty] | Annual Capital Recovery Factor = | 0.143 | Mercury Sorbent Injection
[6 empty] | Annual Capital Cost (Including AFUDC), $ = | 736000
[6 empty] | Annual FOM Cost, $ = | 42000
[6 empty] | Annual VOM Cost, $ = | 7997000
[6 empty] | Total Annual SCR Cost, $ = | 8775000
[6 empty] | Capital Cost, $/MWh = | 0.19769
[6 empty] | FOM Cost, $/MWh = | 0.011281
[6 empty] | VOM Cost, $/MWh = | 2.148
[6 empty] | Total SCR Cost, $/MWh = | 2.357
[6 empty] | Capital Cost, $/ton = | n/a
[6 empty] | FOM Cost, $/ton = | n/a
[6 empty] | VOM Cost, $/ton = | n/a
[6 empty] | Total SCR Cost, $/ton = | n/a
Lookup Table
| Coal | % of Ash | Boiler Removal % | HHV | Flow Rate Multiplier
1 | PRB | 0.06 | 0.2 | 8400 | 0.4
2 | Lignite | 0.08 | 0.2 | 7200 | 0.435
3 | Bituminous | 0.12 | 0.2 | 11000 | 0.362
|  | 0.12 | 0.2 | 11000 | 0.362
1 | Baghouse
2 | ESP
Feed Rate Multiplier |  |  | 5
|  | Std Carbon | Halogen Carbon | Non-Carbon
1 | BGH | 2 | 2 | 3.5
2 | ESP | 5 | 5 | N/A
FGD System
1 | None
2 | Wet FGD
3 | Dry FGD
4 | Other
SCR
Existing | TRUE
FGD? | TRUE
TRUE
Removal | FALSE
FALSE
| Baghouse |  | FALSE
1 | Not Added | 0 | FALSE
2 | 6.0 Air-to-Cloth | 530 | TRUE | 6 | 0.0016777 | 36.6667
3 | 4.0 Air-to-Cloth | 600 | TRUE | 4 | 0.0025165 | 23
Type of Sorbent
1 | Standard PAC
2 | Halogenated PAC
3 | Not Applicable
Aux Power
TRUE

## DSI SO2
Fill in the yellow cells with the known data inputs. The resulting costs are tabulated below. Variable names are defined as outlined in the table.
|  |  | Variable |  |  | Designation | Units | Value | Calculation
|  |  | EPC Project? |  |  |  |  | FALSE
|  |  | Capacity Factor |  |  |  |  | 85
|  |  | Unit Size |  |  | A | (MW) | 500 | <--- User Input (Greater than 100 MW)
|  |  | Retrofit Factor |  |  | B |  | 1 | <--- User Input (An "average" retrofit has a factor = 1.0)
|  |  | Heat Rate |  |  | C | (Btu/kWh) | 9500 | <--- User Input
|  |  | SO2 Rate |  |  | D | (lb/MMBtu) | 2 | <--- User Input
|  |  | Type of Coal |  |  | E |  | 3 | <--- User Input
|  |  | Particulate Capture |  |  | F |  | 1 | <--- User Input
|  |  | Sorbent |  |  | G |  | 1 | <--- User Input
|  |  | Removal Target |  |  | H | (%) | 50 | Maximum Removal Targets: Unmilled Trona with an ESP = 65% Milled Trona with an ESP = 80% Unmilled Trona with a BGH = 80% Milled Trona with a BGH = 90% Hydrated Lime with an ESP = 30% Hydrated Lime with a BGH = 50% |  | Value is BELOW an 80 percent maximum removal target
|  |  | Heat Input |  |  | J | (Btu/hr) | 4750000000 | A*C*1000
|  |  | NSR |  |  | K | (Btu/hr) | 1.4315 | Unmilled Trona with an ESP = if (H<40,0.0350*H,0.352e^(0.0345*H)) Milled Trona with an ESP = if (H<40,0.0270*H,0.353e^(0.0280*H)) Unmilled Trona with an BGH = if (H<40,0.0215*H,0.295e^(0.0267*H)) Milled Trona with an BGH = if (H<40,0.0160*H,0.208e^(0.0281*H)) Hydrated Lime with an ESP = 0.504*H^0.3905 Hydrated Lime with a BGH = 0.0087*H+0.6505
|  |  | Sorbent Feed Rate |  |  | M | (ton/hr) | 16.334 | Trona = (1.2011x10^-06)*K*A*C*D Hydrated Lime =(6.055*(10^-7))*K*A*C*D
|  |  | Estimated HCL Removal |  |  | V | (%) | 92.8946 | Unmilled Trona with an ESP = 60.86*H^0.1081, or 0.002 lb/MMBtu Milled Trona with an ESP = 60.86*H^0.1081, or 0.002 lb/MMBtu Unmilled Trona with an BGH = 0.005*H+97.574, or 0.002 lb/MMBtu Milled Trona with an BGH = 0.005*H+97.574, or 0.002 lb/MMBtu Hydrated Lime with an ESP = 54.92*H^0.197, or 0.002 lb/MMBtu Hydrated Lime with a BGH = 0.0085*H+99.12, or 0.002 lb/MMBtu
|  |  | Sorbent Waste Rate |  |  | N | (ton/hr) | 13.1214 | For Trona (0.7387+0.00185*H/K)*M, Lime = (1.00 + 0.00777*H/K)*M. Waste product adjusted for a maximum of 5% inert in the Trona sorbent and 2% for Hydrated Lime.
|  |  | Fly Ash Waste Rate Include in VOM? |  |  | P | (ton/hr) | 20.7273 | (A*C)*Ash in Coal*(1-Boiler Ash Removal)/(2*HHV) For Bituminous Coal: Ash in Coal = 0.12; Boiler Ash Removal = 0.2; HHV = 11000 For PRB Coal: Ash in Coal = 0.06; Boiler Ash Removal = 0.2; HHV = 8400 For Lignite Coal: Ash in Coal = 0.08; Boiler Ash Removal = 0.2; HHV = 7200
|  |  | Aux Power Include in VOM? |  |  | Q | (%) | 0.65336 | =if Milled Trona M*20/A else M*18/A
|  |  | Sorbent Cost |  |  | R | ($/ton) | 170 | <--- User Input (Trona = $170, Hydrated Lime = $150). In example, unmilled trona = $225
|  |  | Waste Disposal Cost |  |  | S | ($/ton) | 50 | <--- User Input (Disposal cost with fly ash = $50. Without fly ash, the sorbent waste alone will be more dificult to dispose = $100)
|  |  | Aux Power Cost |  |  | T | ($/kWh) | 0.06 | <--- User Input
|  |  | Operating Labor Rate |  |  | U | ($/hr) | 60 | <--- User Input (Labor cost including all benefits)
Costs are all based on 2016 dollars
Capital Cost Calcuation | [8 empty] | Example | Comments
Includes - Equipment, intallation, buildings, foundations, electrical, and retrofit difficulty.
| BM ($) = | Unmilled Trona or hydrated lime if (M>25 then (745,000*B*M) else 7,500,000*B*(M^0.284) Milled Trona if (M>25 then (820,000*B*M) else 8,300,000*B*(M^0.284) | [6 empty] | 18348000 | Base module for unmilled sorbent includes all equipment from unloading to injection, including dehumidification system
| BM ($/kW) = | [7 empty] | 36.696 | Base cost per kW
Total Project Cost
| A1 = 10% of BM | [7 empty] | 1835000 | Engineering and Construction Management costs
| A2= 5% of BM | [7 empty] | 917000 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc…
| A3 = 5% of BM | [7 empty] | 917000 | Contractor profit and fees
| CECC ($) = BM + A1 + A2 + A3 | [7 empty] | 22017000 | Capital, engineering and construction cost subtotal
| CECC ($/kW) = Excludes Owner's Costs = | [7 empty] | 44.034 | Capital, engineering and construction cost subtotal per kW
| B1 = 2% of CECC if EPC TRUE, else 5% of CECC | [7 empty] | 1101000 | Owners costs including all "home office" costs (owners engineering, management, and procuement activities)
| TPC' ($) - Includes Owner's Costs = CECC + B1 | [7 empty] | 23118000 | Total project cost without AFUDC
| TPC' ($/kW) - Includes Owner's Costs | [7 empty] | 46.236 | Total project cost per kW without AFUDC
| B2 = 10% of (CECC + B1) | [7 empty] | 0 | AFUDC (Zero for less than 1 year engineering and construction cycle)
| C1 = if EPC = TRUE, 15% of (CECC+B1), else 0 | [7 empty] | 0 | EPC fees of 15%
| TPC ($) = Includes Owner's Costs and AFUDC = CECC + B1 + B2 + C1 | [7 empty] | 23118000 | Total project cost
| TPC ($/kW) = Includes Owner's Costs and AFUDC | [7 empty] | 46.236 | Total project cost per kW
Fixed O&M Cost
| FOMO ($/kW yr) = (2 additional operators)*2080*U/(A*1000) | [7 empty] | 0.499 | Fixed O&M additional operating labor costs
| FOMM ($/kW yr) =(BM*0.01)/(B*A*1000) | [7 empty] | 0.367 | Fixed O&M additional maintenance material and labor costs
| FOMA ($/kW yr) = 0.03*(FOMO + 0.4*FOMM) | [7 empty] | 0.0194 | Fixed O&M additional administrative labor costs
| FOM ($/kW yr) = FOMO + FOMM + FOMA | [7 empty] | 0.8854 | Total Fixed O&M costs
Variable O&M Cost
| VOMR ($/MWh) = M*R/A | [7 empty] | 5.554 | Variable O&M costs for Trona reagent
| VOMW ($/MWh) = (N+P)*S/A | [7 empty] | 3.385 | Variable O&M costs for waste disposal that includes both the sorbent and the fly ash waste not removed prior to the sorbent injection
| VOMP ($/MWh) = Q*T*10 | [7 empty] | 0.39202 | Variable O&M costs for additional auxiliary power required including additional fan power (Refer to Aux Power % above)
| VOM ($/MWh) = VOMR + VOMW + VOMP | [7 empty] | 9.331 | Total Variable O&M costs
[6 empty] | Annual Capacity Factor = | 85%
[6 empty] | Annual MWhs = | 3723000
[6 empty] | Annual Heat Input MMBtu = | 35368500
[6 empty] | Annual Tons SO2 Created = | 35368.5 | at 100% S conversion
[6 empty] | Annual Tons SO2 Removed = | 17684.25 | at removal efficiency = 50%
[6 empty] | Annual Tons SO2 Emission = | 17684.25
[6 empty] | Annual Avg SO2 Emission Rate, lb/MMBtu = | 1 | Value is AT or ABOVE a 0.1 floor rate
[6 empty] | Trona MMtpy per 1.0 MMtpy SO2 Reduction = | 6.8775
[6 empty] | Annual Capital Recovery Factor = | 0.143 | DSI
[7 empty] | Annual Capital Cost (Including AFUDC), $ = | 3306000
[7 empty] | Annual FOM Cost, $ = | 443000
[7 empty] | Annual VOM Cost, $ = | 34739000
[7 empty] | Total Annual SCR Cost, $ = | 38488000
[7 empty] | Capital Cost, $/MWh = | 0.88799
[7 empty] | FOM Cost, $/MWh = | 0.11899
[7 empty] | VOM Cost, $/MWh = | 9.3309
[7 empty] | Total SCR Cost, $/MWh = | 10.3379
[7 empty] | Capital Cost, $/ton = | 186.946
[7 empty] | FOM Cost, $/ton = | 25.0505
[7 empty] | VOM Cost, $/ton = | 1964.4034
[7 empty] | Total SCR Cost, $/ton = | 2176.3999
Lookup Table
| Removal target |  |  |  | Max Removal | 80
| Particulate | Milled Trona | Unmilled Trona | Hydrated Lime
1 | ESP | 80 | 65 | 30
2 | Baghouse | 90 | 80 | 50
NSR
| Particulate | Milled Trona | Unmilled Trona | Hydrated Lime
1 | ESP | 1.4315 | 1.9756 | 2.3221
2 | Baghouse | 0.84771 | 1.121 | 1.0855
Sorbent Feed Rate
|  | Milled Trona | Unmilled Trona | Hydrated Lime
|  | 16.334 | 16.334 | 8.1669
Estimated HCL Removal
| Particulate | Milled Trona | Unmilled Trona | Hydrated Lime
1 | ESP | 92.8946 | 92.8946 | 118.6937
2 | Baghouse | 97.824 | 97.824 | 99.545
Sorbent Waste Rate
|  | Milled Trona | Unmilled Trona | Hydrated Lime
|  | 13.1214 | 13.1214 | 20.7669
BM
|  | Milled Trona | Unmilled Trona | Hydrated Lime
|  | 18348000 | 16580000 | 16580000
| Coal | % of Ash | Boiler Removal % | HHV | HCl content (lb/mmBtu), average from Table 7-4 Coal Quality Characteristics….in the IPM v6 documentation.
1 | PRB | 0.06 | 0.2 | 8400 | 0.010588
2 | Lignite | 0.08 | 0.2 | 7200 | 0.017778
3 | Bituminous | 0.12 | 0.2 | 11000 | 0.064727
|  | 0.12 | 0.2 | 11000 | 0.064727
Aux Power
TRUE
Fly Ash Waste
TRUE
Sorbent
1 | Milled Trona
2 | Unmilled Trona
3 | Hydrated Lime

## SDA FGD
Fill in the yellow cells with the known data inputs. The resulting costs are tabulated below. Variable names are defined as outlined in the table.
|  |  | Variable | Designation | Units | Value | Calculation
|  |  | EPC Project? |  |  | FALSE
|  |  | Unit Size | A | (MW) | 500 | <--- User Input (Greater than 50 MW)
|  |  | Retrofit Factor | B |  | 1 | <--- User Input (An "average" retrofit has a factor = 1.0)
|  |  | Heat Rate | C | (Btu/kWh) | 9800 | <--- User Input
|  |  | SO2 Rate | D | (lb/MMBtu) | 2 | <--- User Input (SDA FGD Estimation only valid up to 3 lb/MMBtu SO2 Rate)
|  |  | Type of Coal | E |  | 1 | <--- User Input
|  |  | Coal Factor | F |  | 1.05 | Bit = 1.0, PRB = 1.05, Lig = 1.07
|  |  | Heat Rate Factor | G |  | 0.98 | C/10000
|  |  | Heat Input | H | (Btu/hr) | 4900000000 | A*C*1000
|  |  | Capacity Factor | I | (%) | 85 | <--- User Input
|  |  | Operating SO2 Removal | J | (%) | 95 | <--- User Input (Used to adjust actual operating costs)
|  |  | Design Lime Rate | K | (ton/hr) | 7.2326 | (0.6702*(D^2)+13.42*D)*A*G/2000 (Based on 95% SO2 removal)
|  |  | Design Waste Rate | L | (ton/hr) | 16.0695 | (0.8016*(D^2)+31.1917*D)*A*G/2000 (Based on 95% SO2 removal)
|  |  | Aux Power Include in VOM? | M | (%) | 1.3533 | (0.000547*D^2+0.00649*D+1.3)*F*G
|  |  | Makeup Water Rate | N | (1000 gph) | 29.0646 | (0.04898*D^2+0.5925*D+55.11)*A*F*G/1000
|  |  | Lime Cost | P | ($/ton) | 125 | <--- User Input
|  |  | Waste Disposal Cost | Q | ($/ton) | 30 | <--- User Input
|  |  | Aux Power Cost | R | ($/kWh) | 0.06 | <--- User Input
|  |  | Makeup Water Cost | S | ($/kgal) | 1 | <--- User Input
|  |  | Operating Labor Rate | T | ($/hr) | 60 | <--- User Input (Labor cost including all benefits)
Costs are all based on 2016 dollars
Capital Cost Calcuation | [6 empty] | Example | Comments
Includes - Equipment, intallation, buildings, foundations, electrical, and retrofit difficulty.
| BMR ($) = | if (A>600 then (A*98000) else 637000*(A^0.716))*B*(F*G)^0.6*(D/4)^0.01 |  |  |  |  | 55086000 | Base module absorber island cost
| BMF ($) = | if (A>600 then (A*52000) else 338000*(A^0.716))*B*(G*D)^0.2 |  |  |  |  | 33100000 | Base module reagent preparation and waste recycle/handling cost
| BMB ($) = | if (A>600 then (A*138000) else 899000*(A^0.716))*B*(G*F)^0.4 |  |  |  |  | 77837000 | Base balance of plant costs including: ID or booster fans, piping, ductwork modifications and strengthening, electrical, etc...
| BM ($) = | BMR + BMF + BMB |  |  |  |  | 166023000 | Total base module cost including retrofit factor
| BM ($/kW) = | [5 empty] | 332.046 | Base cost per kW
Total Project Cost
| A1 = 10% of BM | [5 empty] | 16602000 | Engineering and Construction Management costs
| A2= 10% of BM | [5 empty] | 16602000 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc…
| A3 = 10% of BM | [5 empty] | 16602000 | Contractor profit and fees
| CECC ($) = BM + A1 + A2 + A3 | [5 empty] | 215829000 | Capital, engineering and construction cost subtotal
| CECC ($/kW) = | [5 empty] | 431.658 | Capital, engineering and construction cost subtotal per kW
| B1 = 2% of CECC if EPC TRUE, else 5% of CECC | [5 empty] | 10791000 | Owners costs including all "home office" costs (owners engineering, management, and procuement activities)
| TPC' ($) - Includes Owner's Costs = CECC + B1 | [5 empty] | 226620000 | Total project cost without AFUDC
| TPC' ($/kW) - Includes Owner's Costs | [5 empty] | 453.24 | Total project cost per kW without AFUDC
| B2 = 10% of (CECC + B1) | [5 empty] | 22662000 | AFUDC (Based on a 3 year engineering and construction cycle)
| C1 = if EPC = TRUE, 15% of (CECC+B1), else 0 | [5 empty] | 0 | EPC fees of 15%
| TPC ($) = Includes Owner's Costs and AFUDC = CECC + B1 + B2 + C1 | [5 empty] | 249282000 | Total project cost
| TPC ($/kW) = Includes Owner's Costs and AFUDC | [5 empty] | 498.564 | Total project cost per kW
Fixed O&M Cost
| FOMO ($/kW yr) = (8 operators)*2080*T/(A*1000) | [5 empty] | 1.997 | Fixed O&M additional operating labor costs
| FOMM ($/kW yr) =(BM*0.015)/(B*A*1000) | [5 empty] | 4.981 | Fixed O&M additional maintenance material and labor costs
| FOMA ($/kW yr) = 0.03*(FOMO + 0.4*FOMM) | [5 empty] | 0.1197 | Fixed O&M additional administrative labor costs
| FOM ($/kW yr) = FOMO +FOMM+FOMA | [5 empty] | 7.0977 | Total Fixed O&M costs
Variable O&M Cost
| VOMR ($/MWh) = K*P/(A*J)/98 | [5 empty] | 1.808 | Variable O&M costs for limestone reagent
| VOMW ($/MWh) = L*Q/(A*J)/98 | [5 empty] | 0.964 | Variable O&M costs for waste disposal
| VOMP ($/MWh) = M*R*10 | [5 empty] | 0.81198 | Variable O&M costs for additional auxiliary power required including additional fan power (Refer to Aux Power % above)
| VOMM ($/MWh) = N*S/A | [5 empty] | 0.058 | Variable O&M costs for makeup water
| VOM ($/MWh) = VOMR + VOMW + VOMP + VOMM | [5 empty] | 3.642 | Total Variable O&M costs
|  |  |  | Annual Capacity Factor = | 85%
|  |  |  | Annual MWhs = | 3723000
|  |  |  | Annual Heat Input MMBtu = | 36485400
|  |  |  | Annual Tons SO2 Created = | 36485.4 | at 100% S conversion
|  |  |  | Annual Tons SO2 Removed = | 34661.13 | at removal efficiency = 95%
|  |  |  | Annual Tons SO2 Emission = | 1824.27
|  |  |  | Annual Avg SO2 Emission Rate, lb/MMBtu = | 0.1 | Value is AT or ABOVE a 0.06 floor rate
|  |  |  | Annual Capital Recovery Factor = | 0.143 | Wet FGD
[5 empty] | Annual Capital Cost (Including AFUDC), $ = | 35647000
[5 empty] | Annual FOM Cost, $ = | 3549000
[5 empty] | Annual VOM Cost, $ = | 13559000
[5 empty] | Total Annual SCR Cost, $ = | 52755000
[5 empty] | Capital Cost, $/MWh = | 9.5748
[5 empty] | FOM Cost, $/MWh = | 0.95326
[5 empty] | VOM Cost, $/MWh = | 3.642
[5 empty] | Total SCR Cost, $/MWh = | 14.17
[5 empty] | Capital Cost, $/ton = | 1028.4431
[5 empty] | FOM Cost, $/ton = | 102.3914
[5 empty] | VOM Cost, $/ton = | 391.1875
[5 empty] | Total SCR Cost, $/ton = | 1522.0219
Lookup Table
| Coal | Coal Factor
1 | PRB | 1.05
2 | Lignite | 1.07
3 | Bituminous | 1
Aux Power
TRUE

## Wet FGD
Fill in the yellow cells with the known data inputs. The resulting costs are tabulated below. Variable names are defined as outlined in the table.
|  |  | Variable | Designation | Units | Value | Calculation
|  |  | EPC Project? |  |  | FALSE
|  |  | Wastewater Treatment |  |  | 2
|  |  | Unit Size | A | (MW) | 500 | <--- User Input (Greater than 100 MW)
|  |  | Retrofit Factor | B |  | 1 | <--- User Input (An "average" retrofit has a factor = 1.0)
|  |  | Heat Rate | C | (Btu/kWh) | 9500 | <--- User Input
|  |  | SO2 Rate | D | (lb/MMBtu) | 3 | <--- User Input
|  |  | Type of Coal | E |  | 3 | <--- User Input
|  |  | Coal Factor | F |  | 1 | Bit = 1.0, PRB = 1.05, Lig = 1.07
|  |  | Heat Rate Factor | G |  | 0.95 | C/10000
|  |  | Heat Input | H | (Btu/hr) | 4750000000 | A*C*1000
|  |  | Capacity Factor | I | (%) | 85 | <--- User Input
|  |  | Operating SO2 Removal | J | (%) | 95 | <--- User Input (Used to adjust actual operating costs)
|  |  | Design Limestone Rate | K | (ton/hr) | 12.483 | 17.52*A*D*G/2000 (Based on 98% removal)
|  |  | Design Waste Rate | L | (ton/hr) | 22.6067 | 1.811*K (Based on 98% removal)
|  |  | Aux Power Include in VOM? | M | (%) | 1.6939 | (1.12e^(0.155*D))*F*G
|  |  | Makeup Water Rate | N | (1000 gph) | 37.8585 | (1.674*D+74.68)*A*F*G/1000
|  |  | Limestone Cost | P | ($/ton) | 30 | <--- User Input
|  |  | Waste Disposal Cost | Q | ($/ton) | 30 | <--- User Input
|  |  | Aux Power Cost | R | ($/kWh) | 0.06 | <--- User Input
|  |  | Makeup Water Cost | S | ($/kgal) | 1 | <--- User Input
|  |  | Operating Labor Rate | T | ($/hr) | 60 | <--- User Input (Labor cost including all benefits)
Costs are all based on 2016 dollars
Capital Cost Calcuation | [6 empty] | Example | Comments
Includes - Equipment, intallation, buildings, foundations, electrical, and retrofit difficulty.
| BMR ($) = | 584000*(B)*((F*G)^0.6)*((D/2)^0.02)*(A^0.716) |  |  |  |  | 48869000 | Base absorber island cost
| BMF ($) = | 202000*(B)*((D*G)^0.3)*(A^0.716) |  |  |  |  | 23674000 | Base reagent preparation cost
| BMW ($) = | 106000*(B)*((D*G)^0.45)*(A^0.716) |  |  |  |  | 14536000 | Base waste handling cost
| BMB ($) = | 1070000*(B)*((F*G)^0.4)*(A^0.716) |  |  |  |  | 89730000 | Base balance of plant costs including: ID or booster fans, new wet chimney, piping, ductwork modifications and strengthening, minor WWT, etc...
| BMWW ($) = | If type is Bio-Chem, then 10600000*(B)*A/500^0.6), else 0 |  |  |  |  | 10600000 | Base wastewater treatment facility, beyond minor physical/chemical treatment
| BM ($) = | BMR + BMF + BMW + BMB + BMWW |  |  |  |  | 187409000 | Total base module cost including retrofit factor
| BM ($/kW) = | [5 empty] | 374.818 | Base cost per kW
Total Project Cost
| A1 = 10% of BM | [5 empty] | 18741000 | Engineering and Construction Management costs
| A2= 10% of BM | [5 empty] | 18741000 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc…
| A3 = 10% of BM | [5 empty] | 18741000 | Contractor profit and fees
| CECC ($) = BM + A1 + A2 + A3 | [5 empty] | 243632000 | Capital, engineering and construction cost subtotal
| CECC ($/kW) = | [5 empty] | 487.264 | Capital, engineering and construction cost subtotal per kW
| B1 = 5% of CECC | [5 empty] | 12182000 | Owners costs including all "home office" costs (owners engineering, management, and procuement activities)
| TPC' ($) - Includes Owner's Costs = CECC + B1 | [5 empty] | 255814000 | Total project cost without AFUDC
| TPC' ($/kW) - Includes Owner's Costs | [5 empty] | 511.628 | Total project cost per kW without AFUDC
| B2 = 10% of (CECC + B1) | [5 empty] | 25581000 | AFUDC (Based on a 3 year engineering and construction cycle)
| C1 = 15% of CECC+B1 | [5 empty] | 0 | EPC fees of 15%
| TPC ($) = Includes Owner's Costs and AFUDC = CECC + B1 + B2 + C1 | [5 empty] | 281395000 | Total project cost
| TPC ($/kW) = Includes Owner's Costs and AFUDC | [5 empty] | 562.79 | Total project cost per kW
Fixed O&M Cost
| FOMO ($/kW yr) = (if MW>500 then 16 additional operators, else 12 operators)*2080*T/(A*1000) | [5 empty] | 2.995 | Fixed O&M additional operating labor costs
| FOMM ($/kW yr) =(BM*0.015)/(B*A*1000) | [5 empty] | 5.622 | Fixed O&M additional maintenance material and labor costs
| FOMA ($/kW yr) = 0.03*(FOMO + 0.4*FOMM) | [5 empty] | 0.1573 | Fixed O&M additional administrative labor costs
| FOMWW ($/kW yr) = | [5 empty] | 0 | Fixed O&M costs for wastewater treatment facility
| FOM ($/kW yr) = FOMO +FOMM+FOMA+ FOMWW | [5 empty] | 8.7743 | Total Fixed O&M costs
Variable O&M Cost
| VOMR ($/MWh) = K*P/(A*J)/98 | [5 empty] | 0.726 | Variable O&M costs for limestone reagent
| VOMW ($/MWh) = L*Q/(A*J)/98 | [5 empty] | 1.315 | Variable O&M costs for waste disposal
| VOMP ($/MWh) = M*R*10 | [5 empty] | 1.0163 | Variable O&M costs for additional auxiliary power required including additional fan power (Refer to Aux Power % above)
| VOMM ($/MWh) = N*S/A | [5 empty] | 0.076 | Variable O&M costs for makeup water
| VOMWW ($/MWh) = | [5 empty] | 0.17 | Variable O&M costs for wastewater treatment facility
| VOM ($/MWh) = VOMR + VOMW + VOMP + VOMM + VOMWW | [5 empty] | 3.3033 | Total Variable O&M costs
|  |  |  | Annual Capacity Factor = | 85%
|  |  |  | Annual MWhs = | 3723000
|  |  |  | Annual Heat Input MMBtu = | 35368500
|  |  |  | Annual Tons SO2 Created = | 53052.75 | at 100% S conversion
|  |  |  | Annual Tons SO2 Removed = | 50400.1125 | at removal efficiency = 95%
|  |  |  | Annual Tons SO2 Emission = | 2652.6375
|  |  |  | Annual Avg SO2 Emission Rate, lb/MMBtu = | 0.15 | Value is AT or ABOVE a 0.06 floor rate
|  |  |  | Annual Capital Recovery Factor = | 0.143 | Wet FGD
[5 empty] | Annual Capital Cost (Including AFUDC), $ = | 40239000
[5 empty] | Annual FOM Cost, $ = | 4387000
[5 empty] | Annual VOM Cost, $ = | 12298000
[5 empty] | Total Annual SCR Cost, $ = | 56924000
[5 empty] | Capital Cost, $/MWh = | 10.8082
[5 empty] | FOM Cost, $/MWh = | 1.1784
[5 empty] | VOM Cost, $/MWh = | 3.3033
[5 empty] | Total SCR Cost, $/MWh = | 15.2898
[5 empty] | Capital Cost, $/ton = | 798.3911
[5 empty] | FOM Cost, $/ton = | 87.0435
[5 empty] | VOM Cost, $/ton = | 244.0074
[5 empty] | Total SCR Cost, $/ton = | 1129.4419
Lookup Table
| Coal | Coal Factor
1 | PRB | 1.05
2 | Lignite | 1.07
3 | Bituminous | 1
Wastewater
1 | Minor physical/chemical | 0
2 | Phys Chem-Biological | 0.17
3 | TBD | 0
Aux Power
TRUE

## SNCR
Fill in the yellow cells with the known data inputs. The resulting costs are tabulated below. Variable names are defined as outlined in the table.
|  |  | Variable | Designation | Units | Value | Calculation
|  |  | Boiler Type | BT |  | 2 | <--- User Input
|  |  | EPC Project? |  |  | FALSE
|  |  | Unit Size | A | (MW) | 500 | <--- User Input
|  |  | Retrofit Factor | B |  | 1 | <--- User Input (An "average" retrofit has a factor = 1.0)
|  |  | Heat Rate | C | (Btu/kWh) | 9800 | <--- User Input
|  |  | NOx Rate | D | (lb/MMBtu) | 0.22 | <--- User Input
|  |  | SO2 Rate | E | (lb/MMBtu) | 2 | <--- User Input
|  |  | Type of Coal | F |  | 3 | <--- User Input
|  |  | Coal Factor | G |  | 1 | Bit = 1.0, PRB = 1.05, Lig = 1.07
|  |  | Heat Rate Factor | H |  | 0.98 | C/10000
|  |  | Heat Input | I | (Btu/hr) | 4900000000 | A*C*1000
|  |  | Capacity Factor | J | (%) | 85 | <--- User Input
|  |  | NOx Removal Efficiency | K | (%) | 25 | <--- User Input
|  |  | NOx Removed | L | (lb/hr) | 269.5 | D*I/10^6*K/100
|  |  | Urea Rate (100%) | M | (lb/hr) | 1171.7391 | L/UF/46*30; If Boiler Type = CFB or D>0.3 THEN UF = 0.25 ELSE UF = 0.15
|  |  | Water Required | N | (lb/hr) | 22263.0435 | M*19
|  |  | Heat Rate Penalty Include in VOM? | V | (%) | 0.53386 | 1175*N/I*100
|  |  | Aux Power Include in VOM? | O | (%) | 0.05 | 0.05 default value
|  |  | Dilution Water Rate | P | (1000 gph) | 2.6693 | N*0.1199/1000
|  |  | Urea Cost (50% wt solution) | Q | ($/ton) | 350 | <--- User Input
|  |  | Aux Power Cost | R | ($/kWh) | 0.06 | <--- User Input
|  |  | Dilution Water Cost | S | ($/klb) | 1 | <--- User Input
|  |  | Operating Labor Rate | T | ($/hr) | 60 | <--- User Input (Labor cost including all benefits)
|  |  | Replacement Coal Cost | U | ($/hr) | 2 | <--- User Input
Costs are all based on 2016 dollars
Capital Cost Calcuation | [6 empty] | Example | Comments
Includes - Equipment, intallation, buildings, foundations, electrical, and retrofit difficulty.
| BMS ($) = | BT*B*G*220000*(A*H)^0.42; IF CFB then BT = 0.75, ELSE BT = 1) |  |  |  |  | 2967000 | SNCR (injectors, blowers, DCS, reagent system) cost
| BMA ($) = | IF E>= 3 and F = Bituminous, THEN 69000*(B)*(A*G*H)^0.78, ELSE 0 |  |  |  |  | 0 | Air heater modifications /SO3 control (Bituminous only and >= 3 lb/MMBtu)
| BMB ($) = | BT*(L^0.12)*320000*(A)^0.33; (IF CFB then BT = 0.75, ELSE BT = 1) |  |  |  |  | 4869000 | Balance of plant costs (piping, site upgrades, water treatment for the dilution water, etc…)
| BM ($) = | BMS + BMA + BMB |  |  |  |  | 7836000 | Total base module cost including retrofit factor
| BM ($/kW) = | [5 empty] | 15.672 | Base cost per kW
Total Project Cost
| A1 = 10% of BM | [5 empty] | 784000 | Engineering and Construction Management costs
| A2= 10% of BM | [5 empty] | 784000 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc…
| A3 = 10% of BM | [5 empty] | 784000 | Contractor profit and fees
| CECC ($) = BM + A1 + A2 + A3 | [5 empty] | 10188000 | Capital, engineering and construction cost subtotal
| CECC ($/kW) = | [5 empty] | 20.376 | Capital, engineering and construction cost subtotal per kW
| B1 = 5% of CECC | [5 empty] | 509000 | Owners costs including all "home office" costs (owners engineering, management, and procuement activities)
| TPC' ($) - Includes Owner's Costs = CECC + B1 | [5 empty] | 10697000 | Total project cost without AFUDC
| TPC' ($/kW) - Includes Owner's Costs | [5 empty] | 21.394 | Total project cost per kW without AFUDC
| B2 = 0% of (CECC + B1) | [5 empty] | 0 | AFUDC (Zero for less than 1 year engineering and construction cycle)
| C1 = if EPC = TRUE, 15% of (CECC+B1), else 0 | [5 empty] | 0 | EPC fees of 15%
| TPC ($) = CECC + B1 + B2 + C1 | [5 empty] | 10697000 | Total project cost
| TPC ($/kW) = | [5 empty] | 21.394 | Total project cost per kW
Fixed O&M Cost
| FOMO ($/kW yr) = (No operator time assumed)*2080*T/(A*1000) | [5 empty] | 0 | Fixed O&M additional operating labor costs
| FOMM ($/kW yr) =(0.012*BM)/(B*A*1000) | [5 empty] | 0.19 | Fixed O&M additional maintenance material and labor costs
| FOMA ($/kW yr) = 0.03*(FOMO + 0.4*FOMM) | [5 empty] | 0.0023 | Fixed O&M additional administrative labor costs
| FOM ($/kW yr) = FOMO +FOMM+FOMA | [5 empty] | 0.1923 | Total Fixed O&M costs
Variable O&M Cost
| VOMR ($/MWh) = M*Q/(A*1000) | [5 empty] | 0.82 | Variable O&M costs for Urea
| VOMM ($/MWh) = P*S/A | [5 empty] | 0.005 | Variable O&M costs for dilution water
| VOMP ($/MWh) = O*R*10 | [5 empty] | 0.03 | Variable O&M costs for additional auxiliary power required.
| VOMB ($/MWh) = 0.001175*N*U/A | [5 empty] | 0.10464 | Variable O&M costs for heat rate increase due to water injected into the boiler
| VOM ($/MWh) = VOMR + VOMW + VOMP + VOMM | [5 empty] | 0.95964 | Total Variable O&M costs
Annual Capacity Factor =
|  |  |  | Annual MWhs = | 85%
|  |  |  | Annual Heat Input MMBtu = | 3723000
|  |  |  | Annual Tons NOx Created = | 36485400
|  |  |  | Annual Tons NOx Removed = | 4013.394 | current NOx Emission
|  |  |  | Annual Tons NOx Emission = | 1003.3485 | at removal efficiency = 25%
|  |  |  | Annual Avg NOx Emission Rate, lb/MMBtu = | 3010.0455
0.165
Annual Capital Recovery Factor =
[5 empty] | 0.143 | SNCR
[5 empty] | Annual Capital Cost (Including AFUDC), $ = | 1530000
[5 empty] | Annual FOM Cost, $ = | 96000
[5 empty] | Annual VOM Cost, $ = | 3573000
[5 empty] | Total Annual SCR Cost, $ = | 5199000
[5 empty] | Capital Cost, $/MWh = | 0.41096
[5 empty] | FOM Cost, $/MWh = | 0.025786
[5 empty] | VOM Cost, $/MWh = | 0.95971
[5 empty] | Total SCR Cost, $/MWh = | 1.3965
[5 empty] | Capital Cost, $/ton = | 1524.8939
[5 empty] | FOM Cost, $/ton = | 95.6796
[5 empty] | VOM Cost, $/ton = | 3561.0757
[5 empty] | Total SCR Cost, $/ton = | 5181.6492
Lookup Table
| Coal | Coal Factor
1 | PRB | 1.05
2 | Lignite | 1.07
3 | Bituminous | 1
Boiler Type
| CFB | 1
| Tangential | 2
| Wall | 3
| Cyclone | 4
Aux Power
TRUE
Heat Rate Penalty
TRUE

## SCR
Fill in the yellow cells with the known data inputs. The resulting costs are tabulated below. Variable names are defined as outlined in the table.
|  |  | Variable | Designation | Units | Value | Calculation
|  |  | EPC Project? |  |  | FALSE
|  |  | Unit Size | A | (MW) | 500 | <--- User Input
|  |  | Retrofit Factor | B |  | 1 | <--- User Input (An "average" retrofit has a factor = 1.0)
|  |  | Heat Rate | C | (Btu/kWh) | 9500 | <--- User Input
|  |  | NOx Rate | D | (lb/MMBtu) | 0.3 | <--- User Input
|  |  | SO2 Rate | E | (lb/MMBtu) | 3 | <--- User Input
|  |  | Type of Coal | F |  | 3 | <--- User Input
|  |  | Coal Factor | G |  | 1 | Bit = 1.0, PRB = 1.05, Lig = 1.07
|  |  | Heat Rate Factor | H |  | 0.95 | C/10000
|  |  | Heat Input | I | (Btu/hr) | 4750000000 | A*C*1000
|  |  | Capacity Factor | J | (%) | 85 | <--- User Input
|  |  | NOx Removal Efficiency | K | (%) | 75 | <--- User Input
|  |  | NOx Removal Factor | L |  | 0.9375 | K/80
|  |  | NOx Removed | M | (lb/hr) | 1068.75 | D*I/10^6*K/100
|  |  | Urea Rate (100%) | N | (lb/hr) | 746.6465 | M*0.525*60/46*1.01/0.99
|  |  | Steam Required | O | (lb/hr) | 844.8305 | N*1.1315
|  |  | Aux Power Include in VOM? | P | (%) | 0.54778 | 0.56*(G*H)^0.43
|  |  | Makeup Water Rate | Q | (1000 gph) | 0
|  |  | Urea Cost (50% wt solution) | R | ($/ton) | 350 | <--- User Input
|  |  | Catalyst Cost | S | ($/m3) | 8000 | <--- User Input
|  |  | Aux Power Cost | T | ($/kWh) | 0.06 | <--- User Input (includes removal and disposal of existing catalyst and installation of new catalyst)
|  |  | Steam Cost | U | ($/klb) | 4 | <--- User Input
|  |  | Operating Labor Rate | V | ($/hr) | 60 | <--- User Input (Labor cost including all benefits)
Costs are all based on 2016 dollars
Capital Cost Calcuation | [6 empty] | Example | Comments
Includes - Equipment, intallation, buildings, foundations, electrical, and retrofit difficulty.
| BMR ($) = | 310000*(B)*(L)^0.2*(A*G*H)^0.92 |  |  |  |  | 88780000 | SCR (ductwork modifications and strengthening, reactor, bypass) island cost
| BMF ($) = | 564000*(M)^0.25 |  |  |  |  | 3225000 | Base reagent preparation cost
| BMA ($) = | IF E>= 3 and F = Bituminous, THEN 69000*(B)*(A*G*H)^0.78, ELSE 0 |  |  |  |  | 8446000 | Air heater modifications /SO3 control (Bituminous only and >= 3 lb/MMBtu)
| BMB ($) = | 529000*(B)*(A*G*H)^0.42 |  |  |  |  | 7042000 | ID or booster fans and auxiliary power modification costs
| BM ($) = | BMR + BMF + BMA + BMB |  |  |  |  | 107493000 | Total base module cost including retrofit factor
| BM ($/kW) = | [5 empty] | 214.986 | Base cost per kW
Total Project Cost
| A1 = 10% of BM | [5 empty] | 10749000 | Engineering and Construction Management costs
| A2= 10% of BM | [5 empty] | 10749000 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc…
| A3 = 10% of BM | [5 empty] | 10749000 | Contractor profit and fees
| CECC ($) = BM + A1 + A2 + A3 | [5 empty] | 139740000 | Capital, engineering and construction cost subtotal
| CECC ($/kW) = | [5 empty] | 279.48 | Capital, engineering and construction cost subtotal per kW
| B1 = 5% of CECC | [5 empty] | 6987000 | Owners costs including all "home office" costs (owners engineering, management, and procuement activities)
| TPC' ($) - Includes Owner's Costs = CECC + B1 | [5 empty] | 146727000 | Total project cost without AFUDC
| TPC' ($/kW) - Includes Owner's Costs | [5 empty] | 293.454 | Total project cost per kW without AFUDC
| B2 = 6% of (CECC + B1) | [5 empty] | 8804000 | AFUDC (Based on a 2 year engineering and construction cycle)
| C1 = if EPC = TRUE, 15% of (CECC+B1), else 0 | [5 empty] | 0 | EPC fees of 15%
| TPC ($) = CECC + B1 + B2 + C1 | [5 empty] | 155531000 | Total project cost
| TPC ($/kW) = | [5 empty] | 311.062 | Total project cost per kW
Fixed O&M Cost
| FOMO ($/kW yr) = 1/2 operator time assumed)*2080*V/(A*1000) | [5 empty] | 0.125 | Fixed O&M additional operating labor costs
| FOMM ($/kW yr) =(IF A < 300 then 0.005*BM ELSE 0.003*BM)/(B*A*1000) | [5 empty] | 0.64 | Fixed O&M additional maintenance material and labor costs
| FOMA ($/kW yr) = 0.03*(FOMO + 0.4*FOMM) | [5 empty] | 0.0114 | Fixed O&M additional administrative labor costs
| FOM ($/kW yr) = FOMO +FOMM+FOMA | [5 empty] | 0.7764 | Total Fixed O&M costs
Variable O&M Cost
| VOMR ($/MWh) = N*R/(A*1000) | [5 empty] | 0.52 | Variable O&M costs for Urea
| VOMW ($/MWh) = (0.4*(G^2.9)*(L^0.71)*S)/(8760) | [5 empty] | 0.34894 | Variable O&M costs for catalyst: replacement & disposal
| VOMP ($/MWh) = P*T*10 | [5 empty] | 0.32867 | Variable O&M costs for additional auxiliary power required including additional fan power
| VOMM ($/MWh) = O*U/A/1000 | [5 empty] | 0.007 | Variable O&M costs for steam
| VOM ($/MWh) = VOMR + VOMW + VOMP + VOMM | [5 empty] | 1.2046 | Total Variable O&M costs
|  |  |  | Annual Capacity Factor = | 85%
|  |  |  | Annual MWhs = | 3723000
|  |  |  | Annual Heat Input MMBtu = | 35368500
|  |  |  | Annual Tons NOx Created = | 5305.275 | current NOx Emission
|  |  |  | Annual Tons NOx Removed = | 3978.9563 | at removal efficiency = 75%
|  |  |  | Annual Tons NOx Emission = | 1326.3187
|  |  |  | Annual Avg NOx Emission Rate, lb/MMBtu = | 0.075 | Value is AT or ABOVE a 0.07 floor rate
|  |  |  | Annual Capital Recovery Factor = | 0.143 | SCR
[5 empty] | Annual Capital Cost (Including AFUDC), $ = | 22241000
[5 empty] | Annual FOM Cost, $ = | 388000
[5 empty] | Annual VOM Cost, $ = | 4485000
[5 empty] | Total Annual SCR Cost, $ = | 27114000
[5 empty] | Capital Cost, $/MWh = | 5.9739
[5 empty] | FOM Cost, $/MWh = | 0.10422
[5 empty] | VOM Cost, $/MWh = | 1.2047
[5 empty] | Total SCR Cost, $/MWh = | 7.2828
[5 empty] | Capital Cost, $/ton = | 5589.6568
[5 empty] | FOM Cost, $/ton = | 97.513
[5 empty] | VOM Cost, $/ton = | 1127.18
[5 empty] | Total SCR Cost, $/ton = | 6814.3499
Lookup Table |  |  | 0.07
| Coal | Coal Factor | NOx Floor Limit
1 | PRB | 1.05 | 0.05
2 | Lignite | 1.07 | 0.05
3 | Bituminous | 1 | 0.07
Aux Power
TRUE