## Introduction
Renewable Natural Gas (RNG) Flow Rate Estimation Tool
Purpose: The Renewable Natural Gas Flow Rate Estimation Tool (RNG Flow Tool) calculates the adjusted flow rate and corresponding heat content (Btu) value of landfill gas (LFG) after adjusting a wellfield to meet the inlet specifications for RNG treatment/processing technology. Raw LFG has a lower Btu content relative to RNG, so LFG must be upgraded with certain treatment technologies to be successfully converted to RNG.
The RNG Flow Tool was developed to provide an approximate estimate of the potential impact on LFG flow rate, Btu content and quality following wellfield adjustment prior to LFG treatment for an LFG-to-RNG energy project. These treatment technologies often specify that the inlet gas quality must contain nitrogen levels lower than what may be typically measured in LFG -- adjusting the LFG collection system to achieve these nitrogen targets may impact the LFG flow rate. The type of RNG delivery method and the associated gas quality specifications for that delivery method or ultimate end use also affect what inlet nitrogen levels are allowable.
To use the RNG Flow Tool, users should enter landfill-specfic data for the current LFG flow rate and the current average nitrogen, methane, carbon dioxide and oxygen concentrations of the LFG as measured at the flare inlet. If landfill-specific average concentrations are unavailable, users may use the provided default concentrations for LFG, based on typical values observed in wellfields that have not been adjusted for RNG energy recovery. The RNG Flow Tool may be used in conjunction with LFGcost-Web to improve the estimates for RNG project costs.
Caveats/Limitations: The calculations in the RNG Flow Tool are based on average concentrations of the LFG and qualitative assessments of the wellfield conditions. The RNG Flow Tool serves as a screening guide to help landfills quickly estimate normalized gas flows for RNG projects. More detailed analysis would be required before pursuing a project that would be based on gas constituent data and wellfield tuning assumptions from each individual well.
This tool does not address "tail gas", methane, Btu content, or flow rate losses from removal of carbon dioxide or other constituents (e.g. siloxanes, hydrogen sulfide) from the LFG.

## Inputs
Renewable Natural Gas (RNG) Flow Rate Estimation Tool
Enter the landfill-specific current LFG flow rate and the current average nitrogen, methane, carbon dioxide and oxygen concentrations of the LFG as measured at the flare inlet. If landfill-specific average concentrations are unavailable, use the provided default concentrations for LFG, based on typical values observed in wellfields that have not been adjusted for RNG energy recovery. Constituent concentrations should sum to 100%.
| Landfill Name: |  |  | Enter Landfill Name Here
| LFG collected flow rate in standard cubic feet per minute (scfm): |  |  |  |  | Direction related to nitrogen values and air intrusion will appear here if warranted:
Typical flow rates for different technologies are presented in the Technology Matrix worksheet.
| Nitrogen (N2) concentration1: |  |  | 10%
Use default of 10% if actual concentration unknown.
| Methane (CH4) concentration: |  |  | 50%
| Use default of 50% if actual concentration unknown. |  |  |  |  | See the 'Technology Matrix' worksheet for more information on LFG-to-RNG treatment technologies that may be suitable for your project. After reviewing the matrix, proceed to Step 2.
| Carbon Dioxide (CO2) concentration2: |  |  | 39%
Use default of 39% if actual concentration unknown.
Constituent total:
| Oxygen (O2) concentration1: |  |  | 1% |  |  | 100% |  | 10
| Use default of 1% if actual concentration unknown. | [6 empty] | N2 to O2 Ratio:
Enter the maximum nitrogen content allowed by the treatment system manufacturer in order to achieve the desired outlet specification for your project. Other main LFG constituents will be automatically updated based on typical values, so that the total equals 100%.
| Nitrogen (N2) concentration for LFG entering the treatment skid1: |  |  | 5% |  |  | CH4 concentration: | 52.5%
Value must be less than or equal to the Nitrogen content in Step 1.
[7 empty] | CO2 concentration2: | 42%
[7 empty] | O2 concentration1: | 0.5%
Review 'Field Condition Ranking Matrix' worksheet and select a corresponding field condition compensation factor. From this step, an adjusted flow rate is calculated to represent the inlet flow rate to the RNG processing plant.
[5 empty] | Calculated inlet flow rate (scfm) to RNG processing plant: |  |  | 0
| Select field condition compensation factor: |  |  | 4
|  | Ranking of field conditions range from most optimal "best" (1) to least optimal "worst" (5) conditions which could affect air infiltration/intrusion in the collection system. Ranking is subjective and varies from site to site, and can only be designated by personnel familiar with the site. |  |  |  |  | at estimated methane content of: | 52.5%
Note: If you are using LFGcost-Web to estimate the cost of an RNG or onsite CNG project, you should select Defined by User as the LFG energy project size in cell D26 of the LFGcost-Web 'INP-OUT' worksheet and enter this inlet flow rate into the project design size in cell D28 of the 'INP-OUT' worksheet. You should also enter the inlet methane content in cell D32 of the 'INP-OUT' worksheet.
| Calculated LFG flow rate reduction factor: |  |  | 1.2155
Select the preferred LFG heating value basis from the drop-down menu if you want to convert the flow rates to heat rates in million Btu per hour (MMBtu/hr). The higher heating value (HHV) is often specified in RNG contracts as it is used in the natural gas industry when specifying minimum acceptable pipeline quality. The lower heating value (LHV) is referenced by LFG energy projects where the loss of heat of combustion due to formation of water is taken into account. The standard loss of heat is 10%.
| Select the basis of heating value of methane: |  | Select the basis of heating value of methane (HHV or LHV) | LHV | Pre-adjustment heat rate of LFG (MMBtu/hr): |  | Pre-adjustment heat rate of LFG (MMBtu/hr) | 0
HHV = 1,012 Btu/scf methane
| LHV = 911 Btu/scf methane |  | LHV = 911 Btu/scf methane
[5 empty] | Post-adjustment heat rate of LFG (MMBtu/hr): |  | Pre-adjustment heat rate of LFG (MMBtu/hr) | 0
| Btu/scf methane: |  |  | 911
NOTES
1. Assumes a nitrogen to oxygen ratio of 10:1, due to the consumption of oxygen during methanogenesis. The residual nitrogen present in the gas is assumed to come predominantly from air infiltration into an active gas collection and control system (GCCS), where the operations have not been optimized for an RNG project. The default nitrogen content in Step 1 is set to 10% (which includes adjustments for nitrogen present due to air leaks). Per the 1997 SWANA O&M guide, the typical normal residual nitrogen in LFG ranges from 6% to 12% (excluding nitrogen from air leaks).a
2. Assumes a methane to carbon dioxide ratio of 1.25:1 for the purpose of this calculator. Ranges of methane and carbon dioxide can vary, but this ratio is typical based on field experience and observations. See 1997 SWANA O&M guide, Table 2.1 for ranges of methane and carbon dioxide.b
HHV
LHV
Step
1
Step
2
Step
3
Step
4
Go to TECHNOLOGY MATRIX for nitrogen ranges for various
LFG-to-RNG treatment technologies.
Go to FIELD CONDITION RANKING MATRIX
Go to OUTPUTS
Go to REFERENCES

## Outputs
LMOP Renewable Natural Gas (RNG) Flow Rate Estimation Tool
Summary Report
Enter Landfill Name Here
2023-01-24 12:49
|  |  | Initial | Adjusted |  | Figure 1: Adjusted Gas Quality
LFG Constituents
| Nitrogen (N2) |  | 10% | 5%
| Methane (CH4) |  | 50% | 52.5%
| Carbon Dioxide (CO2) |  | 39% | 42%
| Oxygen (O2) |  | 1% | 0.5%
| Flow Rate (scfm) |  | 0 | 0
| Heat Rate (MMBtu/hr) |  | 0 | 0
(LHV basis)
| Figure 2: Comparison of Initial and Adjusted LFG Flow Rate |  |  |  | Figure 3: Comparison of Initial and Adjusted LFG Heat Rate
(LHV basis)
Caveats/Limitations: The calculations in the RNG Flow Tool are based on average concentrations of the LFG and qualitative assessments of the wellfield conditions. The RNG Flow Tool serves as a screening guide to help landfills quickly estimate normalized gas flows for RNG projects. More detailed analysis would be required before pursuing a project that would be based on gas constituent data and wellfield tuning assumptions from each individual well.

## Technology Matrix
The following are general descriptions of RNG treatment technologies and their general flow rate and nitrogen handling capabilities. Consult a professional or specific technology vendor for more information.
RNG Treatment Technology | Description | General Flow Rate/ Project Size | General Inlet Nitrogen Range (for vehicle fuel production) | Other Considerations
Membrane - Single Pass | Landfills producing small volumes of LFG often use a relatively simple system in which LFG is compressed through a membrane molecular sieve to separate carbon dioxide from methane. The system is somewhat inefficient by design so that sufficient methane passes through with the carbon dioxide tail gas to allow for combustion in a traditional flare, or for use in an engine, microturbine or boiler. The methane capture efficiency of single pass systems can range from 65 - 80%. | 50 - 400 scfm | 0 - 4% | Membranes configured to remove carbon dioxide are not particularly effective at removing nitrogen from a biogas stream. Membrane systems that remove nitrogen operate at a much higher pressure than that required for carbon dioxide removal. For vehicle fuel applications, nitrogen content in the LFG must be below approximately 4% or a nitrogen rejection system would be required. Utility gas quality requirements for pipeline injection are generally stricter.
Membrane - Multiple Pass | Landfills producing larger volumes of LFG can use a multiple pass membrane system to increase methane capture efficiency. These systems are more costly than their single pass counterparts due to the additional membranes, increased compression requirements and the fact that tail gas must be destroyed in a thermal oxidizer designed to combust the low-Btu tail gas. The methane capture efficiency of multiple pass systems typically ranges from 96 - 99%. | 200 - 5,000+ scfm | 0 - 4%
Pressure Swing Adsorption (PSA) | In PSA systems, an adsorbent media is pressurized with the incoming LFG. A difference in molecular size allows methane to pass through into the product gas while carbon dioxide, and to a lesser extent nitrogen, is captured by the media. Once the media has been saturated, it is depressurized and the carbon dioxide and nitrogen are released into the tail gas stream. A typical PSA system employs multiple vessels operating in different stages of pressurization, depressurization and regeneration. The methane capture efficienicy of PSA systems can range from 95 - 98%, depending on system design. | 50 - 5,000+ scfm | 0 - 12% | A PSA system can be configured with multiple stages to remove nitrogen as well as carbon dioxide. The additional complexity/components required rises as inlet nitrogen content rises.
Solvent Scrubbing | Solvent scrubbing processes use a chemical solvent such as amine or a physical solvent such as Selexol to strip carbon dioxide and hydrogen sulfide from the LFG stream. Carbon dioxide is adsorbed into the solvent allowing methane to pass through into the RNG product stream. In an amine system, the solution is heated in a separate vessel to release the carbon dioxide into the tail gas stream. In a Selexol process, the solvent is depressurized which releases the carbon dioxide. The methane capture efficiency can range from 97 - 99% for physical solvents while it is often >99% for amine solvents. | 1,000 - 5,000+ scfm | 0 - 4% | Solvent scrubbing systems are ineffective at removing nitrogen.
Water Scrubbing | Water scrubbing (sometimes called water wash) is a simple process in which LFG is pressurized into water. Carbon dioxide is adsorbed into the water while the methane passes through into the RNG product gas stream. The water is then depressurized and the carbon dioxide is allowed to pass through in the tail gas. The methane capture efficiency of water scrubbing systems is typically greater than 99%. | 50 - 3,000 scfm | 0 - 4% | Nitrogen is about 100 times less soluble in water than carbon dioxide; therefore very little nitrogen is removed in the water scrubbing process.
Nitrogen Removal - Membrane | Nitrogen removal is often required downstream of the carbon dioxide removal process to ensure RNG meets minimum quality requirements. Membrane nitrogen rejection units (NRUs) are designed to capitalize on the different permeation rate of nitrogen through a membrane as compared to methane. Biogas is compressed to a few hundred pounds per square inch (PSI) and then passed through a membrane, where the nitrogen flows through to the tail gas stream at high pressure and the methane rich product gas exits at a much lower pressure. Some methane flows into the tail gas with the nitrogen. | 400 - 5,000+ scfm | 5 - 8% | Due to their simple design and low maintenance requirements, membrane NRUs are very attractive in applications where nitrogen is at or below approximately 8% in the incoming LFG stream. At higher nitrogen levels, methane capture efficiency is reduced substantially and other processes such as molecular gate provide a better alternative for nitrogen removal.
Nitrogen Removal - PSA | In PSA nitrogen removal systems, an adsorbent media is pressurized with the incoming partially conditioned RNG (carbon dioxide, hydrogen sulfide, moisture and other contaminants have already been removed). A difference in molecular size allows methane to pass through into the product gas while nitrogen is captured by the media. Once the media has been saturated, it is depressurized and the nitrogen is released into the tail gas stream. A typical PSA system employs multiple vessels operating in different stages of pressurization, depressurization and regeneration. | 50 - 5,000+ scfm | 5 - 12% | Nitrogen removal via NRU is typically more costly and complicated than its membrane counterpart, but methane capture efficiency is higher at elevated nitrogen levels. PSA systems also scale well, meaning they become more financially attractive at higher flow rates.
Oxygen Removal | An oxygen removal system utilizes a catalytic reactor to remove oxygen from the biogas stream. As part of the oxygen removal process, the RNG product becomes water saturated, so a moisture removal system is also required at the system outlet. While oxygen removal generally is not necessary for vehicle fuel applications, pipeline injection projects typically have restrictive oxygen limits set by the natural gas utility. These projects often require the removal of oxygen to a fraction of a percent, sometimes even as low as a few parts per million (ppm). | 800 - 5,000+ scfm | - | Due to the added capital and operating costs of incorporating an oxygen removal system, they are often found to be cost-prohibitive for projects with an LFG flow rate less than 1,000 scfm.

## RNG Specifications
RNG End Use or Delivery Method | Description
Since RNG can be a substitute for natural gas, its uses are versatile. For example, RNG can be used in electricity, thermal or vehicle fuel applications. Before RNG can be used it must be delivered from the RNG processing plant to the end user. Delivery methods include injecting into a pipeline or dispensing at a local fueling station in close proximity to the landfill. The main types of vehicle fuel created from LFG are compressed natural gas (CNG) and liquefied natural gas (LNG), with CNG being the most prevalent in the United States. The general specifications listed below are for CNG or injection into a pipeline.
CNG | In the United States, LFG-to-CNG vehicle fuel projects are universally designed to, at a minimum, meet the technical requirements set by the Society of Automotive Engineers Surface Vehicle Recommended Practice J1616 (SAE J1616)a. SAE J1616 sets minimum requirements for CNG fuel composition and properties as delivered to vehicle refueling stations, to ensure vehicle, engine and component durability, safety and performance. SAE J1616 provides technical requirements for several CNG fuel properties and potential constituents including methane, Wobbe Index, sulfur compounds, oxygen, and particulate material. In addition, SAE J1616 references the California Air Resources Board's CNG commercial fuel composition for several specifications, including:
Methane: 88% (minimum)
Oxygen: 1% (maximum)
Sulfur: 16 ppm by volume (maximum)
Inert gases (sum of carbon dioxide and nitrogen): 4.5% (maximum)
Pipeline Injection | Unlike vehicle fuel applications, LFG-to-RNG projects can have outlet gas quality requirements that vary significantly depending on region and local pipeline utilities. In general, the RNG methane content requirement is significantly higher than that required for vehicle fuel, and the level of remaining gases, including moisture, is much lower. It is advisable to reach out to the local utility early in the project feasibility/exploration phase to determine RNG quality requirements as well as how familiar a particular utility is with RNG projects in general.
a Society of Automotive Engineers. Surface Vehicle Recommended Practice J1616. Standard for Compressed Natural Gas Vehicle Fuel. March 2017. Section 4 on Technical Requirements and Appendix D, Table D.2 for CARB Commercial Fuel Composition.
https://www.sae.org/standards/content/j1616_201703/

## Field Condition Ranking Matrix
Field Condition Ranking Matrix
Ranking of field conditions range from most optimal "best" (1) to least optimal "worst" (5) conditions with respect to factors that can affect air infiltration/intrusion in the LFG collection system. Ranking is subjective and varies from site to site, and can only be designated by personnel familiar with the site. The user selects this field condition compensation factor ranking based on site-specific knowledge of the available well and wellhead construction information, lateral and header piping integrity, whether leachate cleanouts are connected to the LFG collection system, wellfield cap condition, and current operations.
Rankings
1 | Best field condition
2 | Intermediate - good field condition
3 | Intermediate - average field condition
4 | Intermediate - poor field condition
5 | Worst field condition
The matrix below presents examples of best and worst field conditions for RNG project applications for different components of the GCCS. Not all of these factors in the matrix need be present to assign a ranking of (1). Similarly, having one or more of the factors ranked as "worst" does not automatically mean the landfill should be assigned a rank of (5).
Conditions | Design and Construction Components | [5 empty] | Operations
| Wells | Wellheads | Header and lateral piping | Leachate cleanouts | Wellfield vacuum/blower | Landfill cap characteristics in areas with active gas wells | Wellfield tuning | Condensate management/ leachate recirculation
Best Field Conditions. Together, these features indicate a lower probability of adjustments being necessary to achieve wellfield operating conditions for an RNG project, and indicate that any adjustments will be effective. Examples of best field conditions for RNG projects include: | Vertical wells with perforations at least 15 feet deep. | Wellheads have fine tuning capabilities. | No leaks in piping/connectors; Tight or redundant seals around well casing. | Not connected to GCCS. | Blower vacuum is stable and blower control logic is employed. The blower control allows LFG flow rate to fluctuate, while holding vacuum steady. | Geomembrane. | Best practices employed for tuning and repairs (e.g., steady vacuum, frequent readings, spare parts available). | Wells are not impacted by condensate or leachate. If well pumping is employed, it is effective in keeping all perforations exposed. Recirculation of leachate is controlled such that the waste mass is not saturated.
Worst Field Conditions indicate a higher need for adjustments necessary to achieve wellfield operating conditions for an RNG project, and indicate that any adjustments will be less effective. Examples of worst field conditions for RNG projects include: | Shallow (<15 feet) perforations in vertical wells or horizontal collectors. | No fine tuning capability. | Leaks in piping or well seals. | Connected to GCCS. | High fluctuations in vacuum. Overpulling vacuum to compensate for low well density (which can result in air intrusion). | No cap or porous cap materials; open active areas. | Substandard wellfield tuning practices. | Wells are "watered-in" by condensate or leachate. Minimal well perforations are exposed. Recirculation of leachate is uncontrolled, saturating the waste, reducing the ability to apply vacuum to the waste mass, while accelerating methane generation rates, causing methane depletion before it can be collected.

## References
a | SWANA. March 1997. Landfill Gas Operation and Maintenance Manual of Practice. Table 9.4.
https://www.nrel.gov/docs/legosti/fy97/23070.pdf
Interpretation of Nitrogen Residual in Landfill Gas
| Residual Nitrogen (%) | Interpretation
| 0 to 6 | Normal to understressed; typical for high BTU [RNG] facility where low nitrogen is desirable.
| 6 to 12 | Normal desirable operating range without compromises for problem landfills.
| 16 to 20 | Excessive nitrogen, may be necessary for aggressive perimeter migration control, side slope emission control, or where other compromise is required.
| Greater than 20 percent | Over-stressed, this level of nitrogen to be avoided if at all possible except for aggressive emission control.
b | SWANA. March 1997. Landfill Gas Operation and Maintenance Manual of Practice. Table 2.1.
https://www.nrel.gov/docs/legosti/fy97/23070.pdf
General Range of Landfill Gas Characteristics
| Component | Percent Volume (All are stated on a dry basis)
| Methane (CH4) | 45 to 58%
| Carbon dioxide (CO2) | 32 to 45%
| Oxygen (O2) | less than 1%
| Nitrogen (N2) | 0 to 3%