## Notes
Notes for example results:
1. All costs are in either 2016$ or 2021$; Capital Costs include Owners Costs and AFUDC.
2. Capital Charge Rate = 14.3% (blended average of utility and merchant owned at 15-yr book life)
3. VOM Cost includes Aux Power at $60/MWh and waste disposal at various $/ton rates
4. In the Dry Sorbent Injection for SO2/HCl Control Cost Development Methodology document, the example utilizes a bituminous coal with an HCl content of 0.04 lb/mmBtu. In the RCA, EPA has created default HCL content values for each coal type using the average from Table 7-4 Coal Quality Characteristics in the IPM v6 documentation. (see "DSI_SO2 worksheet cells B121 through B123).
5. VOM and FOM cost components are typically based on market prices based on the year the Reference Document is finalized. Consequently, adjustments to these values may be warranted to account for inflation and/or changes in base prices.
| Worksheet | Revision Date | Year Dollars in Reference Document | Reference Document
| SNCR_gas | Feb. 2023 | 2021 | SNCR Cost Development Methodology for Oil/Gas-fired Boilers
| SNCR_coal | Feb. 2023 | 2021 | SNCR Cost Development Methodology for Coal-fired Boilers
| SCR_gas | Feb. 2023 | 2021 | SCR Cost Development Methodology for Oil/Gas-fired Boilers
| SCR_coal | Feb. 2023 | 2021 | SCR Cost Development Methodology for Coal-fired Boilers
| DSI | Mar. 2023 | 2021 | Dry Sorbent Injection for SO2/HCl Control Cost Development Methodology
| SDA FGD | Jan. 2017 | 2016 | SDA FGD Cost Development Methodology
| WET FGD | Jan. 2017 | 2016 | Wet FGD Cost Development Methodology

## SNCR_gas
Fill in the yellow cells with the known data inputs. The resulting costs are tabulated below. Variable names are defined as outlined in the table.
|  |  | Variable | Designation | Units | Value | Calculation
|  |  | Boiler Type | BT |  | 2 | <--- User Input
|  |  | EPC Project? |  |  | FALSE
|  |  | Unit Size | A | (MW) | 500 | <--- User Input
|  |  | Retrofit Factor | B |  | 1 | <--- User Input (An "average" retrofit has a factor = 1.0)
|  |  | Heat Rate | C | (Btu/kWh) | 9800 | <--- User Input
|  |  | NOx Rate | D | (lb/MMBtu) | 0.22 | <--- User Input
|  |  | SO2 Rate | E | (lb/MMBtu) | 2 | <--- User Input
|  |  | Type of Fuel | F |  | 1 | <--- User Input
|  |  | Coal Factor | G |  | 1 | Natural gas = 1.0, Oil = 1.06
|  |  | Heat Rate Factor | H |  | 0.98 | C/10000
|  |  | Heat Input | I | (Btu/hr) | 4900000000 | A*C*1000
|  |  | Capacity Factor | J | (%) | 26 | <--- User Input
|  |  | NOx Removal Efficiency | K | (%) | 15 | <--- User Input
|  |  | NOx Removed | L | (lb/hr) | 161.7 | D*I/10^6*K/100
|  |  | Urea Rate (100%) | M | (lb/hr) | 703.0435 | L/UF/46*30; If Boiler Type = CFB or D>0.3 THEN UF = 0.25 ELSE UF = 0.15
|  |  | Water Required | N | (lb/hr) | 13357.8261 | M*19
|  |  | Heat Rate Penalty Include in VOM? | V | (%) | 0.32032 | 1175*N/I*100
|  |  | Aux Power Include in VOM? | O | (%) | 0.05 | 0.05 default value
|  |  | Dilution Water Rate | P | (1000 gph) | 1.6016 | N*0.1199/1000
|  |  | Urea Cost (50% wt solution) | Q | ($/ton) | 350 | <--- User Input
|  |  | Aux Power Cost | R | ($/kWh) | 0.06 | <--- User Input
|  |  | Dilution Water Cost | S | ($/klb) | 1 | <--- User Input
|  |  | Operating Labor Rate | T | ($/hr) | 60 | <--- User Input (Labor cost including all benefits)
|  |  | Replacement Coal Cost | U | ($/hr) | 2 | <--- User Input
Costs are all based on 2021 dollars
Capital Cost Calcuation | [6 empty] | Example | Comments
Includes - Equipment, intallation, buildings, foundations, electrical, and retrofit difficulty.
| BMS ($) = | BT*B*G*202400*(A*H)^0.42; IF CFB then BT = 0.75, ELSE BT = 1) |  |  |  |  | 2730000 | SNCR (injectors, blowers, DCS, reagent system) cost
| BMB ($) = | BT*(L^0.12)*358400*(A)^0.33; (IF CFB then BT = 0.75, ELSE BT = 1) |  |  |  |  | 5129000 | Balance of plant costs (piping, site upgrades, water treatment for the dilution water, etc…)
| BM ($) = | BMS + BMA + BMB |  |  |  |  | 7859000 | Total base module cost including retrofit factor
| BM ($/kW) = | [5 empty] | 15.718 | Base cost per kW
Total Project Cost
| A1 = 10% of BM | [5 empty] | 786000 | Engineering and Construction Management costs
| A2= 10% of BM | [5 empty] | 786000 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc…
| A3 = 10% of BM | [5 empty] | 786000 | Contractor profit and fees
| CECC ($) = BM + A1 + A2 + A3 | [5 empty] | 10217000 | Capital, engineering and construction cost subtotal
| CECC ($/kW) = | [5 empty] | 20.434 | Capital, engineering and construction cost subtotal per kW
| B1 = 5% of CECC | [5 empty] | 511000 | Owners costs including all "home office" costs (owners engineering, management, and procuement activities)
| TPC' ($) - Includes Owner's Costs = CECC + B1 | [5 empty] | 10728000 | Total project cost without AFUDC
| TPC' ($/kW) - Includes Owner's Costs | [5 empty] | 21.456 | Total project cost per kW without AFUDC
| B2 = 0% of (CECC + B1) | [5 empty] | 0 | AFUDC (Zero for less than 1 year engineering and construction cycle)
| C1 = if EPC = TRUE, 15% of (CECC+B1), else 0 | [5 empty] | 0 | EPC fees of 15%
| TPC ($) = CECC + B1 + B2 + C1 | [5 empty] | 10728000 | Total project cost
| TPC ($/kW) = | [5 empty] | 21.456 | Total project cost per kW
Fixed O&M Cost
| FOMO ($/kW yr) = (No operator time assumed)*2080*T/(A*1000) | [5 empty] | 0 | Fixed O&M additional operating labor costs
| FOMM ($/kW yr) =(0.012*BM)/(B*A*1000) | [5 empty] | 0.19 | Fixed O&M additional maintenance material and labor costs
| FOMA ($/kW yr) = 0.03*(FOMO + 0.4*FOMM) | [5 empty] | 0.0023 | Fixed O&M additional administrative labor costs
| FOM ($/kW yr) = FOMO +FOMM+FOMA | [5 empty] | 0.1923 | Total Fixed O&M costs
Variable O&M Cost
| VOMR ($/MWh) = M*Q/(A*1000) | [5 empty] | 0.49 | Variable O&M costs for Urea
| VOMM ($/MWh) = P*S/A | [5 empty] | 0.003 | Variable O&M costs for dilution water
| VOMP ($/MWh) = O*R*10 | [5 empty] | 0.03 | Variable O&M costs for additional auxiliary power required.
| VOMB ($/MWh) = 0.001175*N*U/A | [5 empty] | 0.062782 | Variable O&M costs for heat rate increase due to water injected into the boiler
| VOM ($/MWh) = VOMR + VOMW + VOMP + VOMM | [5 empty] | 0.58578 | Total Variable O&M costs
Annual Capacity Factor =
|  |  |  | Annual MWhs = | 26%
|  |  |  | Annual Heat Input MMBtu = | 1138800
|  |  |  | Annual Tons NOx Created = | 11160240
|  |  |  | Annual Tons NOx Removed = | 1227.6264 | current NOx Emission
|  |  |  | Annual Tons NOx Emission = | 184.144 | at removal efficiency = 15%
|  |  |  | Annual Avg NOx Emission Rate, lb/MMBtu = | 1043.4824
0.187
Annual Capital Recovery Factor =
[5 empty] | 0.143 | SNCR
[5 empty] | Annual Capital Cost (Including AFUDC), $ = | 1534000
[5 empty] | Annual FOM Cost, $ = | 96000
[5 empty] | Annual VOM Cost, $ = | 667000
[5 empty] | Total Annual SNCR Cost, $ = | 2297000
[5 empty] | Capital Cost, $/MWh = | 1.347
[5 empty] | FOM Cost, $/MWh = | 0.084299
[5 empty] | VOM Cost, $/MWh = | 0.5857
[5 empty] | Total SNCR Cost, $/MWh = | 2.017
[5 empty] | Capital Cost, $/ton = | 8330.4389
[5 empty] | FOM Cost, $/ton = | 521.3312
[5 empty] | VOM Cost, $/ton = | 3622.166
[5 empty] | Total SNCR Cost, $/ton = | 12473.9362
Lookup Table
| Fuel | Fuel Factor
1 | Natural gas | 1
2 | Oil | 1.06
Boiler Type
| CFB | 1
| Tangential | 2
| Wall | 3
| Cyclone | 4
Aux Power
TRUE
Heat Rate Penalty
TRUE

## SNCR_coal
Fill in the yellow cells with the known data inputs. The resulting costs are tabulated below. Variable names are defined as outlined in the table.
|  |  | Variable | Designation | Units | Value | Calculation
|  |  | Boiler Type | BT |  | 2 | <--- User Input
|  |  | EPC Project? |  |  | FALSE
|  |  | Unit Size | A | (MW) | 300 | <--- User Input
|  |  | Retrofit Factor | B |  | 1 | <--- User Input (An "average" retrofit has a factor = 1.0)
|  |  | Heat Rate | C | (Btu/kWh) | 9800 | <--- User Input
|  |  | NOx Rate | D | (lb/MMBtu) | 0.22 | <--- User Input
|  |  | SO2 Rate | E | (lb/MMBtu) | 2 | <--- User Input
|  |  | Type of Coal | F |  | 3 | <--- User Input
|  |  | Coal Factor | G |  | 1 | Bit = 1.0, PRB = 1.05, Lig = 1.07
|  |  | Heat Rate Factor | H |  | 0.98 | C/10000
|  |  | Heat Input | I | (Btu/hr) | 2940000000 | A*C*1000
|  |  | Capacity Factor | J | (%) | 56 | <--- User Input
|  |  | NOx Removal Efficiency | K | (%) | 25 | <--- User Input
|  |  | NOx Removed | L | (lb/hr) | 161.7 | D*I/10^6*K/100
|  |  | Urea Rate (100%) | M | (lb/hr) | 703.0435 | L/UF/46*30; If Boiler Type = CFB or D>0.3 THEN UF = 0.25 ELSE UF = 0.15
|  |  | Water Required | N | (lb/hr) | 13357.8261 | M*19
|  |  | Heat Rate Penalty Include in VOM? | V | (%) | 0.53386 | 1175*N/I*100
|  |  | Aux Power Include in VOM? | O | (%) | 0.05 | 0.05 default value
|  |  | Dilution Water Rate | P | (1000 gph) | 1.6016 | N*0.1199/1000
|  |  | Urea Cost (50% wt solution) | Q | ($/ton) | 350 | <--- User Input
|  |  | Aux Power Cost | R | ($/kWh) | 0.06 | <--- User Input
|  |  | Dilution Water Cost | S | ($/klb) | 1 | <--- User Input
|  |  | Operating Labor Rate | T | ($/hr) | 60 | <--- User Input (Labor cost including all benefits)
|  |  | Replacement Coal Cost | U | ($/hr) | 2 | <--- User Input
Costs are all based on 2021 dollars
Capital Cost Calcuation | [6 empty] | Example | Comments
Includes - Equipment, intallation, buildings, foundations, electrical, and retrofit difficulty.
| BMS ($) = | BT*B*G*253000*(A*H)^0.42; IF CFB then BT = 0.75, ELSE BT = 1) |  |  |  |  | 2753000 | SNCR (injectors, blowers, DCS, reagent system) cost
| BMA ($) = | IF E>= 3 and F = Bituminous, THEN 69000*(B)*(A*G*H)^0.78, ELSE 0 |  |  |  |  | 0 | Air heater modifications /SO3 control (Bituminous only and >= 3 lb/MMBtu)
| BMB ($) = | BT*(L^0.12)*448000*(A)^0.33; (IF CFB then BT = 0.75, ELSE BT = 1) |  |  |  |  | 5417000 | Balance of plant costs (piping, site upgrades, water treatment for the dilution water, etc…)
| BM ($) = | BMS + BMA + BMB |  |  |  |  | 8170000 | Total base module cost including retrofit factor
| BM ($/kW) = | [5 empty] | 27.2333 | Base cost per kW
Total Project Cost
| A1 = 10% of BM | [5 empty] | 817000 | Engineering and Construction Management costs
| A2= 10% of BM | [5 empty] | 817000 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc…
| A3 = 10% of BM | [5 empty] | 817000 | Contractor profit and fees
| CECC ($) = BM + A1 + A2 + A3 | [5 empty] | 10621000 | Capital, engineering and construction cost subtotal
| CECC ($/kW) = | [5 empty] | 35.4033 | Capital, engineering and construction cost subtotal per kW
| B1 = 5% of CECC | [5 empty] | 531000 | Owners costs including all "home office" costs (owners engineering, management, and procuement activities)
| TPC' ($) - Includes Owner's Costs = CECC + B1 | [5 empty] | 11152000 | Total project cost without AFUDC
| TPC' ($/kW) - Includes Owner's Costs | [5 empty] | 37.1733 | Total project cost per kW without AFUDC
| B2 = 0% of (CECC + B1) | [5 empty] | 0 | AFUDC (Zero for less than 1 year engineering and construction cycle)
| C1 = if EPC = TRUE, 15% of (CECC+B1), else 0 | [5 empty] | 0 | EPC fees of 15%
| TPC ($) = CECC + B1 + B2 + C1 | [5 empty] | 11152000 | Total project cost
| TPC ($/kW) = | [5 empty] | 37.1733 | Total project cost per kW
Fixed O&M Cost
| FOMO ($/kW yr) = (No operator time assumed)*2080*T/(A*1000) | [5 empty] | 0 | Fixed O&M additional operating labor costs
| FOMM ($/kW yr) =(0.012*BM)/(B*A*1000) | [5 empty] | 0.33 | Fixed O&M additional maintenance material and labor costs
| FOMA ($/kW yr) = 0.03*(FOMO + 0.4*FOMM) | [5 empty] | 0.004 | Fixed O&M additional administrative labor costs
| FOM ($/kW yr) = FOMO +FOMM+FOMA | [5 empty] | 0.334 | Total Fixed O&M costs
Variable O&M Cost
| VOMR ($/MWh) = M*Q/(A*1000) | [5 empty] | 0.82 | Variable O&M costs for Urea
| VOMM ($/MWh) = P*S/A | [5 empty] | 0.005 | Variable O&M costs for dilution water
| VOMP ($/MWh) = O*R*10 | [5 empty] | 0.03 | Variable O&M costs for additional auxiliary power required.
| VOMB ($/MWh) = 0.001175*N*U/A | [5 empty] | 0.10464 | Variable O&M costs for heat rate increase due to water injected into the boiler
| VOM ($/MWh) = VOMR + VOMW + VOMP + VOMM | [5 empty] | 0.95964 | Total Variable O&M costs
Annual Capacity Factor =
|  |  |  | Annual MWhs = | 56%
|  |  |  | Annual Heat Input MMBtu = | 1471680
|  |  |  | Annual Tons NOx Created = | 14422464
|  |  |  | Annual Tons NOx Removed = | 1586.471 | current NOx Emission
|  |  |  | Annual Tons NOx Emission = | 396.6178 | at removal efficiency = 25%
|  |  |  | Annual Avg NOx Emission Rate, lb/MMBtu = | 1189.8533
0.165
Annual Capital Recovery Factor =
[5 empty] | 0.143 | SNCR
[5 empty] | Annual Capital Cost (Including AFUDC), $ = | 1595000
[5 empty] | Annual FOM Cost, $ = | 100000
[5 empty] | Annual VOM Cost, $ = | 1412000
[5 empty] | Total Annual SNCR Cost, $ = | 3107000
[5 empty] | Capital Cost, $/MWh = | 1.0838
[5 empty] | FOM Cost, $/MWh = | 0.06795
[5 empty] | VOM Cost, $/MWh = | 0.95945
[5 empty] | Total SNCR Cost, $/MWh = | 2.1112
[5 empty] | Capital Cost, $/ton = | 4021.5042
[5 empty] | FOM Cost, $/ton = | 252.1319
[5 empty] | VOM Cost, $/ton = | 3560.1028
[5 empty] | Total SNCR Cost, $/ton = | 7833.739
Lookup Table
| Coal | Coal Factor
1 | PRB | 1.05
2 | Lignite | 1.07
3 | Bituminous | 1
Boiler Type
| CFB | 1
| Tangential | 2
| Wall | 3
| Cyclone | 4
Aux Power
TRUE
Heat Rate Penalty
TRUE

## SCR_gas
Fill in the yellow cells with the known data inputs. The resulting costs are tabulated below. Variable names are defined as outlined in the table.
|  |  | Variable | Designation | Units | Value | Calculation
|  |  | EPC Project? |  |  | FALSE
|  |  | Unit Size | A | (MW) | 500 | <--- User Input
|  |  | Retrofit Factor | B |  | 1 | <--- User Input (An "average" retrofit has a factor = 1.0)
|  |  | Heat Rate | C | (Btu/kWh) | 9500 | <--- User Input
|  |  | NOx Rate | D | (lb/MMBtu) | 0.3 | <--- User Input
|  |  | SO2 Rate | E | (lb/MMBtu) | 3 | <--- User Input
|  |  | Type of fuel | F |  | 1 | <--- User Input
|  |  | Fuel Factor | G |  | 1 | Natural gas = 1.0, Oil = 1.06
|  |  | Heat Rate Factor | H |  | 0.95 | C/10000
|  |  | Heat Input | I | (Btu/hr) | 4750000000 | A*C*1000
|  |  | Capacity Factor | J | (%) | 26 | <--- User Input
|  |  | NOx Removal Efficiency | K | (%) | 90 | <--- User Input
|  |  | NOx Removal Factor | L |  | 1.125 | K/80
|  |  | NOx Removed | M | (lb/hr) | 1282.5 | D*I/10^6*K/100
|  |  | Urea Rate (100%) | N | (lb/hr) | 895.9758 | M*0.525*60/46*1.01/0.99
|  |  | Steam Required | O | (lb/hr) | 1013.7966 | N*1.1315
|  |  | Aux Power Include in VOM? | P | (%) | 0.27389 | 0.28*(G*H)^0.43
|  |  | Makeup Water Rate | Q | (1000 gph) | 0
|  |  | Urea Cost (50% wt solution) | R | ($/ton) | 350 | <--- User Input
|  |  | Catalyst Cost | S | ($/m3) | 9000 | <--- User Input
|  |  | Aux Power Cost | T | ($/kWh) | 0.06 | <--- User Input (includes removal and disposal of existing catalyst and installation of new catalyst)
|  |  | Steam Cost | U | ($/klb) | 4 | <--- User Input
|  |  | Operating Labor Rate | V | ($/hr) | 60 | <--- User Input (Labor cost including all benefits)
Costs are all based on 2021 dollars
Capital Cost Calcuation | [6 empty] | Example | Comments
Includes - Equipment, intallation, buildings, foundations, electrical, and retrofit difficulty.
| BMR ($) = | 129500*(B)*(L)^0.2*(A*G*H)^0.92 |  |  |  |  | 38464000 | SCR (ductwork modifications and strengthening, reactor, bypass) island cost
| BMF ($) = | 671000*(M)^0.25 |  |  |  |  | 4015000 | Base reagent preparation cost
| BMB ($) = | 315000*(B)*(A*G*H)^0.42 |  |  |  |  | 4193000 | ID or booster fans and auxiliary power modification costs
| BM ($) = | BMR + BMF + BMA + BMB |  |  |  |  | 46672000 | Total base module cost including retrofit factor
| BM ($/kW) = | [5 empty] | 93.344 | Base cost per kW
Total Project Cost
| A1 = 10% of BM | [5 empty] | 4667000 | Engineering and Construction Management costs
| A2= 10% of BM | [5 empty] | 4667000 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc…
| A3 = 10% of BM | [5 empty] | 4667000 | Contractor profit and fees
| CECC ($) = BM + A1 + A2 + A3 | [5 empty] | 60673000 | Capital, engineering and construction cost subtotal
| CECC ($/kW) = | [5 empty] | 121.346 | Capital, engineering and construction cost subtotal per kW
| B1 = 5% of CECC | [5 empty] | 3034000 | Owners costs including all "home office" costs (owners engineering, management, and procuement activities)
| TPC' ($) - Includes Owner's Costs = CECC + B1 | [5 empty] | 63707000 | Total project cost without AFUDC
| TPC' ($/kW) - Includes Owner's Costs | [5 empty] | 127.414 | Total project cost per kW without AFUDC
| B2 = 6% of (CECC + B1) | [5 empty] | 3822000 | AFUDC (Based on a 2 year engineering and construction cycle)
| C1 = if EPC = TRUE, 15% of (CECC+B1), else 0 | [5 empty] | 0 | EPC fees of 15%
| TPC ($) = CECC + B1 + B2 + C1 | [5 empty] | 67529000 | Total project cost
| TPC ($/kW) = | [5 empty] | 135.058 | Total project cost per kW
Fixed O&M Cost
| FOMO ($/kW yr) = 1/2 operator time assumed)*2080*V/(A*1000) | [5 empty] | 0.125 | Fixed O&M additional operating labor costs
| FOMM ($/kW yr) =(IF A < 300 then 0.005*BM ELSE 0.003*BM)/(B*A*1000) | [5 empty] | 0.28 | Fixed O&M additional maintenance material and labor costs
| FOMA ($/kW yr) = 0.03*(FOMO + 0.4*FOMM) | [5 empty] | 0.0071 | Fixed O&M additional administrative labor costs
| FOM ($/kW yr) = FOMO +FOMM+FOMA | [5 empty] | 0.4121 | Total Fixed O&M costs
Variable O&M Cost
| VOMR ($/MWh) = N*R/(A*1000) | [5 empty] | 0.63 | Variable O&M costs for Urea
| VOMW ($/MWh) = (0.065*(G^2.9)*(L^0.71)*S)/(8760) | [5 empty] | 0.072606 | Variable O&M costs for catalyst: replacement & disposal
| VOMP ($/MWh) = P*T*10 | [5 empty] | 0.16434 | Variable O&M costs for additional auxiliary power required including additional fan power
| VOMM ($/MWh) = O*U/A/1000 | [5 empty] | 0.008 | Variable O&M costs for steam
| VOM ($/MWh) = VOMR + VOMW + VOMP + VOMM | [5 empty] | 0.87494 | Total Variable O&M costs
|  |  |  | Annual Capacity Factor = | 26%
|  |  |  | Annual MWhs = | 1138800
|  |  |  | Annual Heat Input MMBtu = | 10818600
|  |  |  | Annual Tons NOx Created = | 1622.79 | current NOx Emission
|  |  |  | Annual Tons NOx Removed = | 1460.511 | at removal efficiency = 90%
|  |  |  | Annual Tons NOx Emission = | 162.279
|  |  |  | Annual Avg NOx Emission Rate, lb/MMBtu = | 0.03 | Value is AT or ABOVE a 0.02 floor rate
|  |  |  | Annual Capital Recovery Factor = | 0.143 | SCR
[5 empty] | Annual Capital Cost (Including AFUDC), $ = | 9657000
[5 empty] | Annual FOM Cost, $ = | 206000
[5 empty] | Annual VOM Cost, $ = | 996000
[5 empty] | Total Annual SCR Cost, $ = | 10859000
[5 empty] | Capital Cost, $/MWh = | 8.48
[5 empty] | FOM Cost, $/MWh = | 0.18089
[5 empty] | VOM Cost, $/MWh = | 0.8746
[5 empty] | Total SCR Cost, $/MWh = | 9.5355
[5 empty] | Capital Cost, $/ton = | 6612.0693
[5 empty] | FOM Cost, $/ton = | 141.0465
[5 empty] | VOM Cost, $/ton = | 681.9531
[5 empty] | Total SCR Cost, $/ton = | 7435.069
Lookup Table |  |  | 0.02
| Fuel | Fuel Factor | NOx Floor Limit (this is expected to range from 0.02 to 0.05 lb/mmBtu)
1 | Natural gas | 1 | 0.02
2 | Oil | 1.06 | 0.02
Aux Power
TRUE

## SCR_coal
Fill in the yellow cells with the known data inputs. The resulting costs are tabulated below. Variable names are defined as outlined in the table.
|  |  | Variable | Designation | Units | Value | Calculation
|  |  | EPC Project? |  |  | FALSE
|  |  | Unit Size | A | (MW) | 500 | <--- User Input
|  |  | Retrofit Factor | B |  | 1 | <--- User Input (An "average" retrofit has a factor = 1.0)
|  |  | Heat Rate | C | (Btu/kWh) | 9500 | <--- User Input
|  |  | NOx Rate | D | (lb/MMBtu) | 0.3 | <--- User Input
|  |  | SO2 Rate | E | (lb/MMBtu) | 3 | <--- User Input
|  |  | Type of Coal | F |  | 3 | <--- User Input
|  |  | Coal Factor | G |  | 1 | Bit = 1.0, PRB = 1.05, Lig = 1.07
|  |  | Heat Rate Factor | H |  | 0.95 | C/10000
|  |  | Heat Input | I | (Btu/hr) | 4750000000 | A*C*1000
|  |  | Capacity Factor | J | (%) | 85 | <--- User Input
|  |  | NOx Removal Efficiency | K | (%) | 75 | <--- User Input
|  |  | NOx Removal Factor | L |  | 0.9375 | K/80
|  |  | NOx Removed | M | (lb/hr) | 1068.75 | D*I/10^6*K/100
|  |  | Urea Rate (100%) | N | (lb/hr) | 746.6465 | M*0.525*60/46*1.01/0.99
|  |  | Steam Required | O | (lb/hr) | 844.8305 | N*1.1315
|  |  | Aux Power Include in VOM? | P | (%) | 0.54778 | 0.56*(G*H)^0.43
|  |  | Makeup Water Rate | Q | (1000 gph) | 0
|  |  | Urea Cost (50% wt solution) | R | ($/ton) | 350 | <--- User Input
|  |  | Catalyst Cost | S | ($/m3) | 9000 | <--- User Input
|  |  | Aux Power Cost | T | ($/kWh) | 0.06 | <--- User Input (includes removal and disposal of existing catalyst and installation of new catalyst)
|  |  | Steam Cost | U | ($/klb) | 4 | <--- User Input
|  |  | Operating Labor Rate | V | ($/hr) | 60 | <--- User Input (Labor cost including all benefits)
Costs are all based on 2021 dollars
Capital Cost Calcuation | [6 empty] | Example | Comments
Includes - Equipment, intallation, buildings, foundations, electrical, and retrofit difficulty.
| BMR ($) = | 370000*(B)*(L)^0.2*(A*G*H)^0.92 |  |  |  |  | 105963000 | SCR (ductwork modifications and strengthening, reactor, bypass) island cost
| BMF ($) = | 671000*(M)^0.25 |  |  |  |  | 3837000 | Base reagent preparation cost
| BMA ($) = | IF E>= 3 and F = Bituminous, THEN 60000*(B)*(A*G*H)^0.78, ELSE 0 |  |  |  |  | 7345000 | Air heater modifications /SO3 control (Bituminous only and >= 3 lb/MMBtu) For SO3 control cost refer to PJFF+PM2.5 spreadsheet
| BMB ($) = | 630000*(B)*(A*G*H)^0.42 |  |  |  |  | 8386000 | ID or booster fans and auxiliary power modification costs
| BM ($) = | BMR + BMF + BMA + BMB |  |  |  |  | 125531000 | Total base module cost including retrofit factor
| BM ($/kW) = | [5 empty] | 251.062 | Base cost per kW
Total Project Cost
| A1 = 10% of BM | [5 empty] | 12553000 | Engineering and Construction Management costs
| A2= 10% of BM | [5 empty] | 12553000 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc…
| A3 = 10% of BM | [5 empty] | 12553000 | Contractor profit and fees
| CECC ($) = BM + A1 + A2 + A3 | [5 empty] | 163190000 | Capital, engineering and construction cost subtotal
| CECC ($/kW) = | [5 empty] | 326.38 | Capital, engineering and construction cost subtotal per kW
| B1 = 5% of CECC | [5 empty] | 8160000 | Owners costs including all "home office" costs (owners engineering, management, and procuement activities)
| TPC' ($) - Includes Owner's Costs = CECC + B1 | [5 empty] | 171350000 | Total project cost without AFUDC
| TPC' ($/kW) - Includes Owner's Costs | [5 empty] | 342.7 | Total project cost per kW without AFUDC
| B2 = 6% of (CECC + B1) | [5 empty] | 10281000 | AFUDC (Based on a 2 year engineering and construction cycle)
| C1 = if EPC = TRUE, 15% of (CECC+B1), else 0 | [5 empty] | 0 | EPC fees of 15%
| TPC ($) = CECC + B1 + B2 + C1 | [5 empty] | 181631000 | Total project cost
| TPC ($/kW) = | [5 empty] | 363.262 | Total project cost per kW
Fixed O&M Cost
| FOMO ($/kW yr) = 1/2 operator time assumed)*2080*V/(A*1000) | [5 empty] | 0.125 | Fixed O&M additional operating labor costs
| FOMM ($/kW yr) =(IF A < 300 then 0.005*BM ELSE 0.003*BM)/(B*A*1000) | [5 empty] | 0.75 | Fixed O&M additional maintenance material and labor costs
| FOMA ($/kW yr) = 0.03*(FOMO + 0.4*FOMM) | [5 empty] | 0.0128 | Fixed O&M additional administrative labor costs
| FOM ($/kW yr) = FOMO +FOMM+FOMA | [5 empty] | 0.8878 | Total Fixed O&M costs
Variable O&M Cost
| VOMR ($/MWh) = N*R/(A*1000) | [5 empty] | 0.52 | Variable O&M costs for Urea
| VOMW ($/MWh) = (0.4*(G^2.9)*(L^0.71)*S)/(8760) | [5 empty] | 0.39255 | Variable O&M costs for catalyst: replacement & disposal
| VOMP ($/MWh) = P*T*10 | [5 empty] | 0.32867 | Variable O&M costs for additional auxiliary power required including additional fan power
| VOMM ($/MWh) = O*U/A/1000 | [5 empty] | 0.007 | Variable O&M costs for steam
| VOM ($/MWh) = VOMR + VOMW + VOMP + VOMM | [5 empty] | 1.2482 | Total Variable O&M costs
|  |  |  | Annual Capacity Factor = | 85%
|  |  |  | Annual MWhs = | 3723000
|  |  |  | Annual Heat Input MMBtu = | 35368500
|  |  |  | Annual Tons NOx Created = | 5305.275 | current NOx Emission
|  |  |  | Annual Tons NOx Removed = | 3978.9563 | at removal efficiency = 75%
|  |  |  | Annual Tons NOx Emission = | 1326.3187
|  |  |  | Annual Avg NOx Emission Rate, lb/MMBtu = | 0.075 | Value is AT or ABOVE a 0.05 floor rate
|  |  |  | Annual Capital Recovery Factor = | 0.143 | SCR
[5 empty] | Annual Capital Cost (Including AFUDC), $ = | 25973000
[5 empty] | Annual FOM Cost, $ = | 444000
[5 empty] | Annual VOM Cost, $ = | 4647000
[5 empty] | Total Annual SCR Cost, $ = | 31064000
[5 empty] | Capital Cost, $/MWh = | 6.9764
[5 empty] | FOM Cost, $/MWh = | 0.11926
[5 empty] | VOM Cost, $/MWh = | 1.2482
[5 empty] | Total SCR Cost, $/MWh = | 8.3438
[5 empty] | Capital Cost, $/ton = | 6527.5912
[5 empty] | FOM Cost, $/ton = | 111.5871
[5 empty] | VOM Cost, $/ton = | 1167.8942
[5 empty] | Total SCR Cost, $/ton = | 7807.0725
Lookup Table |  |  | 0.05
| Coal | Coal Factor | NOx Floor Limit (lb/mmBtu)
1 | PRB | 1.05 | 0.05
2 | Lignite | 1.07 | 0.05
3 | Bituminous | 1 | 0.05
Aux Power
TRUE

## DSI
Fill in the yellow cells with the known data inputs. The resulting costs are tabulated below. Variable names are defined as outlined in the table.
|  |  | Variable |  |  | Designation | Units | Value | Calculation
|  |  | EPC Project? |  |  |  |  | FALSE
|  |  | Capacity Factor |  |  |  |  | 85
|  |  | Unit Size |  |  | A | (MW) | 500 | <--- User Input (Greater than 100 MW)
|  |  | Retrofit Factor |  |  | B |  | 1 | <--- User Input (An "average" retrofit has a factor = 1.0)
|  |  | Heat Rate |  |  | C | (Btu/kWh) | 9500 | <--- User Input
|  |  | SO2 Rate |  |  | D | (lb/MMBtu) | 1 | <--- User Input
|  |  | Type of Coal |  |  | E |  | 3 | <--- User Input
|  |  | Particulate Capture |  |  | F |  | 1 | <--- User Input
|  |  | Sorbent |  |  | G |  | 4 | <--- User Input
|  |  | Removal Target |  |  | H | (%) | 95 | Maximum Removal Targets: Unmilled Trona with an ESP = 70% Milled Trona with an ESP = 85% Unmilled Trona with a BGH = 85% Milled Trona with a BGH = 90% Sodium Bicarbonate (SBC) with an ESP = 95% Sodium Bicarbonate (SBC) with a BGH = 98% Hydrated Lime with an ESP = 40% Hydrated Lime with a BGH = 50% |  | Value is AT or ABOVE an 40 percent maximum removal target
|  |  | Heat Input |  |  | J | (Btu/hr) | 4750000000 | A*C*1000
|  |  | NSR |  |  | K | (Btu/hr) | 15.5887 | Unmilled Trona with an ESP = if (H<40,0.0310*H,0.352e^(0.0313*H)) Milled Trona with an ESP = if (H<40,0.0245*H,0.355e^(0.0254*H)) Unmilled Trona with an BGH = if (H<40, 0.0196*H, 0.296e^(0.0242*H)) Milled Trona with an BGH = if (H<40, 0.0150*H, 0.220e^(0.0255*H)) Sodium Bicarbonate (SBC) with an ESP = if (H<60, 0.0185*H, 0.255e^(0.0248*H)) Sodium Bicarbonate (SBC) with a BGH = if (H<60,0.0120*H, 0.165e^(0.0243*H)) Hydrated Lime with an ESP = if (H<10, 0.34*H^0.51, 0.82EXP(0.031*H)) Hydrated Lime with a BGH = if (H<10, 0.40*H^0.31, 0.62EXP(0.025*H))
|  |  | Sorbent Feed Rate |  |  | M | (ton/hr) | 44.4686 | Trona = (1.2011x10^-06)*K*A*C*D Hydrated Lime =(6.055*(10^-7))*K*A*C*D Sodium Bicarbonate =(1.3125x10^-06)*K*A*C*D
|  |  | Estimated HCL Removal |  |  | V | (%) | 95.9308 | Unmilled Trona with an ESP = 60.86*H^0.1081, or 0.002 lb/MMBtu Milled Trona with an ESP = 60.86*H^0.1081, or 0.002 lb/MMBtu Unmilled Trona with an BGH = 84.598*H^0.0346, or 0.002 lb/MMBtu Milled Trona with an BGH = 84.598*H^0.0346, or 0.002 lb/MMBtu Sodium Bicarbonate with an ESP = 60.86*H^0.1081, or 0.002 lb/MMBtu Sodium Bicarbonate with a BGH = 84.598*H^0.0346, or 0.002 lb/MMBtu Hydrated Lime with an ESP = 54.92*H^0.197, or 0.002 lb/MMBtu Hydrated Lime with a BGH = 0.0085*H+99.12, or 0.002 lb/MMBtu
|  |  | Sorbent Waste Rate |  |  | N | (ton/hr) | 46.5743 | Trona (0.7387+0.002372*H/K)*M, Lime = (1.00 + 0.00777*H/K)*M. Sodium Bicarbonate = (0.6310 + 0.003143*H/K)*M. Waste product adjusted for a maximum of 5% inert in the Trona sorbent and 2% for Hydrated Lime and 0% for Sodium Bicarbonate.
|  |  | Fly Ash Waste Rate Include in VOM? |  |  | P | (ton/hr) | 20.7273 | (A*C)*Ash in Coal*(1-Boiler Ash Removal)/(2*HHV) For Bituminous Coal: Ash in Coal = 0.12; Boiler Ash Removal = 0.2; HHV = 11000 For PRB Coal: Ash in Coal = 0.06; Boiler Ash Removal = 0.2; HHV = 8400 For Lignite Coal: Ash in Coal = 0.08; Boiler Ash Removal = 0.2; HHV = 7200
|  |  | Aux Power Include in VOM? |  |  | Q | (%) | 1.6009 | =if Milled Trona M*20/A else M*18/A
|  |  | Sorbent Cost |  |  | R | ($/ton) | 150 | <--- User Input (Trona = $270, Hydrated Lime = $150, Sodium Bicarbonate = $380)
|  |  | Waste Disposal Cost |  |  | S | ($/ton) | 50 | <--- User Input (Disposal cost with fly ash = $50. Without fly ash, the sorbent waste alone will be more dificult to dispose = $100)
|  |  | Aux Power Cost |  |  | T | ($/kWh) | 0.06 | <--- User Input
|  |  | Operating Labor Rate |  |  | U | ($/hr) | 60 | <--- User Input (Labor cost including all benefits)
Costs are all based on 2021 dollars
Capital Cost Calcuation | [8 empty] | Example | Comments
Includes - Equipment, intallation, buildings, foundations, electrical, and retrofit difficulty.
| BM ($) = | Unmilled Trona if (M>25 then (860,000*B*M) else 6,290,000*B*(M^0.378) Milled Trona if (M>25 then (950,000*B*M) else 6,970,000*B*(M^0.378) Hydrated Lime if (M>25 then (910,000*B*M) else 6,690,000*B*(M^0.378) Sodium Bicarbonate if (M>25 then (920,000*B*M) else 6,730,000*B*(M^0.378) | [6 empty] | 40466465.6657 | Base module for unmilled sorbent includes all equipment from unloading to injection, including dehumidification system
| BM ($/kW) = | [7 empty] | 80.9329 | Base cost per kW
Total Project Cost
| A1 = 10% of BM | [7 empty] | 4047000 | Engineering and Construction Management costs
| A2= 5% of BM | [7 empty] | 2023000 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc…
| A3 = 5% of BM | [7 empty] | 2023000 | Contractor profit and fees
| CECC ($) = BM + A1 + A2 + A3 | [7 empty] | 48559465.6657 | Capital, engineering and construction cost subtotal
| CECC ($/kW) = Excludes Owner's Costs = | [7 empty] | 97.1189 | Capital, engineering and construction cost subtotal per kW
| B1 = 2% of CECC if EPC TRUE, else 5% of CECC | [7 empty] | 2428000 | Owners costs including all "home office" costs (owners engineering, management, and procuement activities)
| TPC' ($) - Includes Owner's Costs = CECC + B1 | [7 empty] | 50987465.6657 | Total project cost without AFUDC
| TPC' ($/kW) - Includes Owner's Costs | [7 empty] | 101.9749 | Total project cost per kW without AFUDC
| B2 = 10% of (CECC + B1) | [7 empty] | 0 | AFUDC (Zero for less than 1 year engineering and construction cycle)
| C1 = if EPC = TRUE, 15% of (CECC+B1), else 0 | [7 empty] | 0 | EPC fees of 15%
| TPC ($) = Includes Owner's Costs and AFUDC = CECC + B1 + B2 + C1 | [7 empty] | 50987465.6657 | Total project cost
| TPC ($/kW) = Includes Owner's Costs and AFUDC | [7 empty] | 101.9749 | Total project cost per kW
Fixed O&M Cost
| FOMO ($/kW yr) = (2 additional operators)*2080*U/(A*1000) | [7 empty] | 0.499 | Fixed O&M additional operating labor costs
| FOMM ($/kW yr) =(BM*0.01)/(B*A*1000) | [7 empty] | 0.809 | Fixed O&M additional maintenance material and labor costs
| FOMA ($/kW yr) = 0.03*(FOMO + 0.4*FOMM) | [7 empty] | 0.0247 | Fixed O&M additional administrative labor costs
| FOM ($/kW yr) = FOMO + FOMM + FOMA | [7 empty] | 1.3327 | Total Fixed O&M costs
Variable O&M Cost
| VOMR ($/MWh) = M*R/A | [7 empty] | 13.341 | Variable O&M costs for Trona reagent
| VOMW ($/MWh) = (N+P)*S/A | [7 empty] | 6.73 | Variable O&M costs for waste disposal that includes both the sorbent and the fly ash waste not removed prior to the sorbent injection
| VOMP ($/MWh) = Q*T*10 | [7 empty] | 0.96052 | Variable O&M costs for additional auxiliary power required including additional fan power (Refer to Aux Power % above)
| VOM ($/MWh) = VOMR + VOMW + VOMP | [7 empty] | 21.0315 | Total Variable O&M costs
[6 empty] | Annual Capacity Factor = | 85%
[6 empty] | Annual MWhs = | 3723000
[6 empty] | Annual Heat Input MMBtu = | 35368500
[6 empty] | Annual Tons SO2 Created = | 17684.25 | at 100% S conversion
[6 empty] | Annual Tons SO2 Removed = | 16800.0375 | at removal efficiency = 95%
[6 empty] | Annual Tons SO2 Emission = | 884.2125
[6 empty] | Annual Avg SO2 Emission Rate, lb/MMBtu = | 0.05 | Value is BELOW a 0.1 lb/MMBtu emission rate
[6 empty] | Trona MMtpy per 1.0 MMtpy SO2 Reduction = | 19.7091
[6 empty] | Annual Capital Recovery Factor = | 0.143 | DSI
[7 empty] | Annual Capital Cost (Including AFUDC), $ = | 7291000
[7 empty] | Annual FOM Cost, $ = | 666000
[7 empty] | Annual VOM Cost, $ = | 78300000
[7 empty] | Total Annual DSI Cost, $ = | 86257000
[7 empty] | Capital Cost, $/MWh = | 1.9584
[7 empty] | FOM Cost, $/MWh = | 0.17889
[7 empty] | VOM Cost, $/MWh = | 21.0314
[7 empty] | Total DSI Cost, $/MWh = | 23.1687
[7 empty] | Capital Cost, $/ton = | 433.9871
[7 empty] | FOM Cost, $/ton = | 39.6428
[7 empty] | VOM Cost, $/ton = | 4660.7039
[7 empty] | Total DSI Cost, $/ton = | 5134.3338
Lookup Table
| Removal target |  |  |  | Max Removal | 40
| Particulate | Milled Trona | Unmilled Trona | Sodium Bicarbonate (SBC) | Hydrated Lime
1 | ESP | 85 | 70 | 95 | 40
2 | Baghouse | 90 | 85 | 98 | 50
NSR
| Particulate | Milled Trona | Unmilled Trona | Sodium Bicarbonate (SBC) | Hydrated Lime
1 | ESP | 3.9644 | 6.8852 | 2.6899 | 15.5887
2 | Baghouse | 2.4803 | 2.9494 | 1.6598 | 6.6656
Sorbent Feed Rate
|  | Milled Trona | Unmilled Trona | Sodium Bicarbonate (SBC) | Hydrated Lime
|  | 88.9373 | 88.9373 | 97.1861 | 44.4686
Estimated HCL Removal
| Particulate | Milled Trona | Unmilled Trona | Sodium Bicarbonate (SBC) | Hydrated Lime
1 | ESP | 99.5689 | 99.5689 | 99.5689 | 134.6921 | 95.9308
2 | Baghouse | 99.0351 | 99.0351 | 99.0351 | 99.9275
Sorbent Waste Rate
|  | Milled Trona | Unmilled Trona | Sodium Bicarbonate (SBC) | Hydrated Lime
|  | 33.4918 | 33.4918 | 28.6405 | 46.5743
BM
|  | Milled Trona | Unmilled Trona | Sodium Bicarbonate (SBC) | Hydrated Lime
|  | 42245211.4092 | 38243033.4863 | 40911152.1016 | 40466465.6657
| Coal | % of Ash | Boiler Removal % | HHV | HCl content (lb/mmBtu), average from Table 7-4 Coal Quality Characteristics in the IPM v6 documentation.
1 | PRB | 0.06 | 0.2 | 8400 | 0.010588
2 | Lignite | 0.08 | 0.2 | 7200 | 0.017778
3 | Bituminous | 0.12 | 0.2 | 11000 | 0.049149
|  | 0.12 | 0.2 | 11000 | 0.049149
Aux Power
TRUE
Fly Ash Waste
TRUE
Sorbent
1 | Milled Trona
2 | Unmilled Trona
3 | Sodium Bicarbonate (SBC)
4 | Hydrated Lime
Default Trona Cost
|  | Milled Trona | Unmilled Trona | Sodium Bicarbonate (SBC) | Hydrated Lime
|  | 270 | 270 | 380 | 150

## SDA FGD
Fill in the yellow cells with the known data inputs. The resulting costs are tabulated below. Variable names are defined as outlined in the table.
|  |  | Variable | Designation | Units | Value | Calculation
|  |  | EPC Project? |  |  | FALSE
|  |  | Unit Size | A | (MW) | 500 | <--- User Input (Greater than 50 MW)
|  |  | Retrofit Factor | B |  | 1 | <--- User Input (An "average" retrofit has a factor = 1.0)
|  |  | Heat Rate | C | (Btu/kWh) | 9800 | <--- User Input
|  |  | SO2 Rate | D | (lb/MMBtu) | 2 | <--- User Input (SDA FGD Estimation only valid up to 3 lb/MMBtu SO2 Rate)
|  |  | Type of Coal | E |  | 1 | <--- User Input
|  |  | Coal Factor | F |  | 1.05 | Bit = 1.0, PRB = 1.05, Lig = 1.07
|  |  | Heat Rate Factor | G |  | 0.98 | C/10000
|  |  | Heat Input | H | (Btu/hr) | 4900000000 | A*C*1000
|  |  | Capacity Factor | I | (%) | 85 | <--- User Input
|  |  | Operating SO2 Removal | J | (%) | 95 | <--- User Input (Used to adjust actual operating costs)
|  |  | Design Lime Rate | K | (ton/hr) | 7.2326 | (0.6702*(D^2)+13.42*D)*A*G/2000 (Based on 95% SO2 removal)
|  |  | Design Waste Rate | L | (ton/hr) | 16.0695 | (0.8016*(D^2)+31.1917*D)*A*G/2000 (Based on 95% SO2 removal)
|  |  | Aux Power Include in VOM? | M | (%) | 1.3533 | (0.000547*D^2+0.00649*D+1.3)*F*G
|  |  | Makeup Water Rate | N | (1000 gph) | 29.0646 | (0.04898*D^2+0.5925*D+55.11)*A*F*G/1000
|  |  | Lime Cost | P | ($/ton) | 125 | <--- User Input
|  |  | Waste Disposal Cost | Q | ($/ton) | 30 | <--- User Input
|  |  | Aux Power Cost | R | ($/kWh) | 0.06 | <--- User Input
|  |  | Makeup Water Cost | S | ($/kgal) | 1 | <--- User Input
|  |  | Operating Labor Rate | T | ($/hr) | 60 | <--- User Input (Labor cost including all benefits)
Costs are all based on 2016 dollars
Capital Cost Calcuation | [6 empty] | Example | Comments
Includes - Equipment, intallation, buildings, foundations, electrical, and retrofit difficulty.
| BMR ($) = | if (A>600 then (A*98000) else 637000*(A^0.716))*B*(F*G)^0.6*(D/4)^0.01 |  |  |  |  | 55086000 | Base module absorber island cost
| BMF ($) = | if (A>600 then (A*52000) else 338000*(A^0.716))*B*(G*D)^0.2 |  |  |  |  | 33100000 | Base module reagent preparation and waste recycle/handling cost
| BMB ($) = | if (A>600 then (A*138000) else 899000*(A^0.716))*B*(G*F)^0.4 |  |  |  |  | 77837000 | Base balance of plant costs including: ID or booster fans, piping, ductwork modifications and strengthening, electrical, etc...
| BM ($) = | BMR + BMF + BMB |  |  |  |  | 166023000 | Total base module cost including retrofit factor
| BM ($/kW) = | [5 empty] | 332.046 | Base cost per kW
Total Project Cost
| A1 = 10% of BM | [5 empty] | 16602000 | Engineering and Construction Management costs
| A2= 10% of BM | [5 empty] | 16602000 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc…
| A3 = 10% of BM | [5 empty] | 16602000 | Contractor profit and fees
| CECC ($) = BM + A1 + A2 + A3 | [5 empty] | 215829000 | Capital, engineering and construction cost subtotal
| CECC ($/kW) = | [5 empty] | 431.658 | Capital, engineering and construction cost subtotal per kW
| B1 = 2% of CECC if EPC TRUE, else 5% of CECC | [5 empty] | 10791000 | Owners costs including all "home office" costs (owners engineering, management, and procuement activities)
| TPC' ($) - Includes Owner's Costs = CECC + B1 | [5 empty] | 226620000 | Total project cost without AFUDC
| TPC' ($/kW) - Includes Owner's Costs | [5 empty] | 453.24 | Total project cost per kW without AFUDC
| B2 = 10% of (CECC + B1) | [5 empty] | 22662000 | AFUDC (Based on a 3 year engineering and construction cycle)
| C1 = if EPC = TRUE, 15% of (CECC+B1), else 0 | [5 empty] | 0 | EPC fees of 15%
| TPC ($) = Includes Owner's Costs and AFUDC = CECC + B1 + B2 + C1 | [5 empty] | 249282000 | Total project cost
| TPC ($/kW) = Includes Owner's Costs and AFUDC | [5 empty] | 498.564 | Total project cost per kW
Fixed O&M Cost
| FOMO ($/kW yr) = (8 operators)*2080*T/(A*1000) | [5 empty] | 1.997 | Fixed O&M additional operating labor costs
| FOMM ($/kW yr) =(BM*0.015)/(B*A*1000) | [5 empty] | 4.981 | Fixed O&M additional maintenance material and labor costs
| FOMA ($/kW yr) = 0.03*(FOMO + 0.4*FOMM) | [5 empty] | 0.1197 | Fixed O&M additional administrative labor costs
| FOM ($/kW yr) = FOMO +FOMM+FOMA | [5 empty] | 7.0977 | Total Fixed O&M costs
Variable O&M Cost
| VOMR ($/MWh) = K*P/(A*J)/98 | [5 empty] | 1.808 | Variable O&M costs for limestone reagent
| VOMW ($/MWh) = L*Q/(A*J)/98 | [5 empty] | 0.964 | Variable O&M costs for waste disposal
| VOMP ($/MWh) = M*R*10 | [5 empty] | 0.81198 | Variable O&M costs for additional auxiliary power required including additional fan power (Refer to Aux Power % above)
| VOMM ($/MWh) = N*S/A | [5 empty] | 0.058 | Variable O&M costs for makeup water
| VOM ($/MWh) = VOMR + VOMW + VOMP + VOMM | [5 empty] | 3.642 | Total Variable O&M costs
|  |  |  | Annual Capacity Factor = | 85%
|  |  |  | Annual MWhs = | 3723000
|  |  |  | Annual Heat Input MMBtu = | 36485400
|  |  |  | Annual Tons SO2 Created = | 36485.4 | at 100% S conversion
|  |  |  | Annual Tons SO2 Removed = | 34661.13 | at removal efficiency = 95%
|  |  |  | Annual Tons SO2 Emission = | 1824.27
|  |  |  | Annual Avg SO2 Emission Rate, lb/MMBtu = | 0.1 | Value is AT or ABOVE a 0.08 floor rate
|  |  |  | Annual Capital Recovery Factor = | 0.143 | Wet FGD
[5 empty] | Annual Capital Cost (Including AFUDC), $ = | 35647000
[5 empty] | Annual FOM Cost, $ = | 3549000
[5 empty] | Annual VOM Cost, $ = | 13559000
[5 empty] | Total Annual SDA FGD Cost, $ = | 52755000
[5 empty] | Capital Cost, $/MWh = | 9.5748
[5 empty] | FOM Cost, $/MWh = | 0.95326
[5 empty] | VOM Cost, $/MWh = | 3.642
[5 empty] | Total SDA FGD Cost, $/MWh = | 14.17
[5 empty] | Capital Cost, $/ton = | 1028.4431
[5 empty] | FOM Cost, $/ton = | 102.3914
[5 empty] | VOM Cost, $/ton = | 391.1875
[5 empty] | Total SDA FGD Cost, $/ton = | 1522.0219
Lookup Table
| Coal | Coal Factor
1 | PRB | 1.05
2 | Lignite | 1.07
3 | Bituminous | 1
Aux Power
TRUE

## Wet FGD
Fill in the yellow cells with the known data inputs. The resulting costs are tabulated below. Variable names are defined as outlined in the table.
|  |  | Variable | Designation | Units | Value | Calculation
|  |  | EPC Project? |  |  | FALSE
|  |  | Wastewater Treatment |  |  | 2
|  |  | Unit Size | A | (MW) | 500 | <--- User Input (Greater than 100 MW)
|  |  | Retrofit Factor | B |  | 1 | <--- User Input (An "average" retrofit has a factor = 1.0)
|  |  | Heat Rate | C | (Btu/kWh) | 9500 | <--- User Input
|  |  | SO2 Rate | D | (lb/MMBtu) | 3 | <--- User Input
|  |  | Type of Coal | E |  | 3 | <--- User Input
|  |  | Coal Factor | F |  | 1 | Bit = 1.0, PRB = 1.05, Lig = 1.07
|  |  | Heat Rate Factor | G |  | 0.95 | C/10000
|  |  | Heat Input | H | (Btu/hr) | 4750000000 | A*C*1000
|  |  | Capacity Factor | I | (%) | 56 | <--- User Input
|  |  | Operating SO2 Removal | J | (%) | 95 | <--- User Input (Used to adjust actual operating costs)
|  |  | Design Limestone Rate | K | (ton/hr) | 12.483 | 17.52*A*D*G/2000 (Based on 98% removal)
|  |  | Design Waste Rate | L | (ton/hr) | 22.6067 | 1.811*K (Based on 98% removal)
|  |  | Aux Power Include in VOM? | M | (%) | 1.6939 | (1.12e^(0.155*D))*F*G
|  |  | Makeup Water Rate | N | (1000 gph) | 37.8585 | (1.674*D+74.68)*A*F*G/1000
|  |  | Limestone Cost | P | ($/ton) | 30 | <--- User Input
|  |  | Waste Disposal Cost | Q | ($/ton) | 30 | <--- User Input
|  |  | Aux Power Cost | R | ($/kWh) | 0.06 | <--- User Input
|  |  | Makeup Water Cost | S | ($/kgal) | 1 | <--- User Input
|  |  | Operating Labor Rate | T | ($/hr) | 60 | <--- User Input (Labor cost including all benefits)
Costs are all based on 2016 dollars
Capital Cost Calcuation | [6 empty] | Example | Comments
Includes - Equipment, intallation, buildings, foundations, electrical, and retrofit difficulty.
| BMR ($) = | 584000*(B)*((F*G)^0.6)*((D/2)^0.02)*(A^0.716) |  |  |  |  | 48869000 | Base absorber island cost
| BMF ($) = | 202000*(B)*((D*G)^0.3)*(A^0.716) |  |  |  |  | 23674000 | Base reagent preparation cost
| BMW ($) = | 106000*(B)*((D*G)^0.45)*(A^0.716) |  |  |  |  | 14536000 | Base waste handling cost
| BMB ($) = | 1070000*(B)*((F*G)^0.4)*(A^0.716) |  |  |  |  | 89730000 | Base balance of plant costs including: ID or booster fans, new wet chimney, piping, ductwork modifications and strengthening, minor WWT, etc...
| BMWW ($) = | If type is Bio-Chem, then 10600000*(B)*A/500^0.6), else 0 |  |  |  |  | 10600000 | Base wastewater treatment facility, beyond minor physical/chemical treatment
| BM ($) = | BMR + BMF + BMW + BMB + BMWW |  |  |  |  | 187409000 | Total base module cost including retrofit factor
| BM ($/kW) = | [5 empty] | 374.818 | Base cost per kW
Total Project Cost
| A1 = 10% of BM | [5 empty] | 18741000 | Engineering and Construction Management costs
| A2= 10% of BM | [5 empty] | 18741000 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc…
| A3 = 10% of BM | [5 empty] | 18741000 | Contractor profit and fees
| CECC ($) = BM + A1 + A2 + A3 | [5 empty] | 243632000 | Capital, engineering and construction cost subtotal
| CECC ($/kW) = | [5 empty] | 487.264 | Capital, engineering and construction cost subtotal per kW
| B1 = 5% of CECC | [5 empty] | 12182000 | Owners costs including all "home office" costs (owners engineering, management, and procuement activities)
| TPC' ($) - Includes Owner's Costs = CECC + B1 | [5 empty] | 255814000 | Total project cost without AFUDC
| TPC' ($/kW) - Includes Owner's Costs | [5 empty] | 511.628 | Total project cost per kW without AFUDC
| B2 = 10% of (CECC + B1) | [5 empty] | 25581000 | AFUDC (Based on a 3 year engineering and construction cycle)
| C1 = 15% of CECC+B1 | [5 empty] | 0 | EPC fees of 15%
| TPC ($) = Includes Owner's Costs and AFUDC = CECC + B1 + B2 + C1 | [5 empty] | 281395000 | Total project cost
| TPC ($/kW) = Includes Owner's Costs and AFUDC | [5 empty] | 562.79 | Total project cost per kW
Fixed O&M Cost
| FOMO ($/kW yr) = (if MW>500 then 16 additional operators, else 12 operators)*2080*T/(A*1000) | [5 empty] | 2.995 | Fixed O&M additional operating labor costs
| FOMM ($/kW yr) =(BM*0.015)/(B*A*1000) | [5 empty] | 5.622 | Fixed O&M additional maintenance material and labor costs
| FOMA ($/kW yr) = 0.03*(FOMO + 0.4*FOMM) | [5 empty] | 0.1573 | Fixed O&M additional administrative labor costs
| FOMWW ($/kW yr) = | [5 empty] | 0 | Fixed O&M costs for wastewater treatment facility
| FOM ($/kW yr) = FOMO +FOMM+FOMA+ FOMWW | [5 empty] | 8.7743 | Total Fixed O&M costs
Variable O&M Cost
| VOMR ($/MWh) = K*P/(A*J)/98 | [5 empty] | 0.726 | Variable O&M costs for limestone reagent
| VOMW ($/MWh) = L*Q/(A*J)/98 | [5 empty] | 1.315 | Variable O&M costs for waste disposal
| VOMP ($/MWh) = M*R*10 | [5 empty] | 1.0163 | Variable O&M costs for additional auxiliary power required including additional fan power (Refer to Aux Power % above)
| VOMM ($/MWh) = N*S/A | [5 empty] | 0.076 | Variable O&M costs for makeup water
| VOMWW ($/MWh) = | [5 empty] | 0.17 | Variable O&M costs for wastewater treatment facility
| VOM ($/MWh) = VOMR + VOMW + VOMP + VOMM + VOMWW | [5 empty] | 3.3033 | Total Variable O&M costs
|  |  |  | Annual Capacity Factor = | 56%
|  |  |  | Annual MWhs = | 2452800
|  |  |  | Annual Heat Input MMBtu = | 23301600
|  |  |  | Annual Tons SO2 Created = | 34952.4 | at 100% S conversion
|  |  |  | Annual Tons SO2 Removed = | 33204.78 | at removal efficiency = 95%
|  |  |  | Annual Tons SO2 Emission = | 1747.62
|  |  |  | Annual Avg SO2 Emission Rate, lb/MMBtu = | 0.15 | Value is AT or ABOVE a 0.06 floor rate
|  |  |  | Annual Capital Recovery Factor = | 0.143 | Wet FGD
[5 empty] | Annual Capital Cost (Including AFUDC), $ = | 40239000
[5 empty] | Annual FOM Cost, $ = | 4387000
[5 empty] | Annual VOM Cost, $ = | 8102000
[5 empty] | Total Annual Wet FGD Cost, $ = | 52728000
[5 empty] | Capital Cost, $/MWh = | 16.4053
[5 empty] | FOM Cost, $/MWh = | 1.7886
[5 empty] | VOM Cost, $/MWh = | 3.3032
[5 empty] | Total Wet FGD Cost, $/MWh = | 21.4971
[5 empty] | Capital Cost, $/ton = | 1211.8436
[5 empty] | FOM Cost, $/ton = | 132.1195
[5 empty] | VOM Cost, $/ton = | 244.001
[5 empty] | Total Wet FGD Cost, $/ton = | 1587.9641
Lookup Table
| Coal | Coal Factor
1 | PRB | 1.05
2 | Lignite | 1.07
3 | Bituminous | 1
Wastewater
1 | Minor physical/chemical | 0
2 | Phys Chem-Biological | 0.17
3 | TBD | 0
Aux Power
TRUE