| EPA Region 8 Drinking Water Unit Finished Water Storage Tank Inspection: Air Vent Fill out one checklist per storage tank & submit labeled photos of each tank component with this form |  |  |  |
| --- | --- | --- | --- |
| PWS Name: | PWS ID: |  |  |
| Tank Name: | Tank ID: |  |  |
| Proposed Inspection Date: | Actual Inspection Date: |  |  |
| Name of Person Filling Out Form: | Title of Person Filling Out Form: |  |  |
| I certify that this information is complete and accurate: |  | Date: |  |

| Inspector Qualifications (answer to all questions must be “yes” if entering a confined space) |  |
| --- | --- |
| Name and contact information of inspector (if water system personnel) or inspection company: |  |
| Yes No | Has the inspector completed confined space training? |
| Yes No | Did the inspector have a confined space entry permit? |

| Overall Tank Condition |  |  |  |  |
| --- | --- | --- | --- | --- |
| Significant Deficiency |  | Required Correction | Proposed Completion Date | Actual Completion Date |
| Yes No | Does the tank appear to be structurally sound? | If no, what repairs are suggested by the tank inspector? |  |  |
| Yes No | Are there any unprotected openings in the tank (breaches, leaks, daylight coming through tank in spots, etc) | If yes, indicate type of breach and how it should be repaired. |  |  |

| Air Vent |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Significant Deficiency |  |  | Required Correction | Proposed Completion Date | Actual Completion Date |
| Yes No NA |  | Does the tank have a vent separate from the overflow? | If no, indicate proposed correction: |  |  |
| Above Ground Tanks (Ground Level or Elevated) Check if NA |  |  |  |  |  |
| Yes No NA | Downturned vent: Is the vent at least 24” above the roof? |  | If no reconfigure vent to provide proper air gap. |  |  |
| Yes No NA | Non-downturned vent: Is there a solid cover down to the bottom of the vent screen? |  | If no, indicate deficiency and proposed correction: |  |  |
| Yes No NA | Non-downturned vent: Is the screen at least 8” above the roof surface? What is the height of the start of the screening above the tank? |  | If no, indicate deficiency and proposed correction: |  |  |
| Yes No | Is the vent covered with #24 mesh corrosion resistant screening (some exceptions apply)? Mesh Size: |  | If no, indicate deficiency and proposed correction: |  |  |
| Buried or Partially Buried Tanks Check if NA |  |  |  |  |  |
| Yes No | Is the vent covered with #24 mesh corrosion resistant screening? |  | If no, install proper #24 mesh corrosion resistant screening. |  |  |
| Yes No | Does the air vent terminate downward? |  | If no, re-configure the vent so that it terminates downward. |  |  |
| Yes No | Is the air vent at least 24” above the tank roof or ground surface (whichever is higher)? What is the height of the vent above the roof or ground surface? |  | If no, raise air vent to provide for an appropriate air gap. |  |  |