| EPA Region 8 Drinking Water Unit Finished Water Storage Tank Inspection: Overflow Fill out one checklist per storage tank & submit labeled photos of each tank component with this form |  |  |  |
| --- | --- | --- | --- |
| PWS Name: | PWS ID: |  |  |
| Tank Name: | Tank ID: |  |  |
| Proposed Inspection Date: | Actual Inspection Date: |  |  |
| Name of Person Filling Out Form: | Title of Person Filling Out Form: |  |  |
| I certify that this information is complete and accurate: |  | Date: |  |

| Inspector Qualifications (answer to all questions must be “yes” if entering a confined space) |  |
| --- | --- |
| Name and contact information of inspector (if water system personnel) or inspection company: |  |
| Yes No | Has the inspector completed confined space training? |
| Yes No | Did the inspector have a confined space entry permit? |

| Overall Tank Condition |  |  |  |  |
| --- | --- | --- | --- | --- |
| Significant Deficiency |  | Required Correction | Proposed Completion Date | Actual Completion Date |
| Yes No | Does the tank appear to be structurally sound? | If no, what repairs are suggested by the tank inspector? |  |  |
| Yes No | Are there any unprotected openings in the tank (breaches, leaks, daylight coming through tank in spots, etc) | If yes, indicate type of breach and how it should be repaired. |  |  |

| Overflow |  |  |  |  |
| --- | --- | --- | --- | --- |
| Significant Deficiency |  | Required Correction | Proposed Completion Date | Actual Completion Date |
| Yes No NA | Does the tank have an overflow separate from the vent? | If no, indicate proposed correction: |  |  |
| Yes No | Discharge has #24 mesh corrosion resistant screen OR a duckbill valve OR a properly sealed flapper valve with a screen inside (EPA recommends #24 mesh screen)? | If no, indicate proposed correction: |  |  |
| Yes No | Overflow terminates between 12 and 24 inches above the ground surface? At what height does the overflow discharge? | If no, modify overflow to provide for an appropriate air gap. |  |  |
| Yes No | Overflow discharges over an inlet structure, splash plate, or engineered rip-rap? | If no, indicate proposed correction: |  |  |
| Yes No NA | Does the overflow have an air gap of 3 or more pipe diameters above the entrance to any storm or sanitary sewers? | If yes, indicate proposed correction: |  |  |
| Yes No | Is there blockage in the overflow, an inadequately sized overflow, a malfunction of the level control system, or other issue that is causing the tank to overflow through the hatch or vent? | If yes, indicate what is causing the problem and how it should be repaired: |  |  |
| Yes No | Is the overflow discharge point visible? If no, the discharge point must be made visible so it can be inspected. |  |  |  |